## summer
[11 empty] | 时间 | 风机盘管1 | 风机盘管2 | 风机盘管3 | 时间 | 排风机总功率 | 排风机2 | 时间
工况 | 夏季主机设定供水温度/℃ | 风机盘管运行档位 | 冬季主机设定供水温度/℃ | 冬季供暖末端运行模式 | [6 empty] | 9:20 | 38.4 | 81.6 | 81.6 | 9:20 | 26.4 |  | 9:20 | 602.4 | 1.323 | 144576
1 | 8 | 低 | 45 | 仅风机盘管 | [6 empty] | 9:30 | 38.4 | 81.6 | 81.6 | 9:30 | 26.4 |  | 9:30 | 422.4 | 5.673 | 101376
2 | 8 | 中 | 45 | 仅风机盘管 | [6 empty] | 9:40 | 38.4 | 81.6 | 81.6 | 9:40 | 26.4 |  | 9:40 | 336 | 6.009 | 80640
3 | 8 | 高 | 45 | 仅风机盘管 | [6 empty] | 9:50 | 38.4 | 81.6 | 81.6 | 9:50 | 26.4 |  | 9:50 | 271.2 | 5.317 | 65088
4 | 10 | 低 | 45 | 仅风机盘管 | [6 empty] | 10:00 | 38.4 | 81.6 | 81.6 | 10:00 | 26.4 |  | 10:00 | 204 | 3.378 | 48960
5 | 10 | 中 | 45 | 仅风机盘管 | [6 empty] | 10:10 | 38.4 | 81.6 | 81.6 | 10:10 | 26.4 |  | 10:10 | 268.8 | 3.135 | 64512
6 | 10 | 高 | 45 | 仅风机盘管 | [6 empty] | 10:20 | 38.4 | 81.6 | 81.6 | 10:20 | 26.4 |  | 10:20 | 218.4 | 5.16 | 52416
7 | 12 | 低 | 45 | 仅风机盘管 | [6 empty] | 10:30 | 38.4 | 81.6 | 81.6 | 10:30 | 26.4 |  | 10:30 | 345.6 | 2.535 | 82944
8 | 12 | 中 | 45 | 仅风机盘管 | [6 empty] | 10:40 | 38.4 | 81.6 | 81.6 | 10:40 | 26.4 |  | 10:40 | 283.2 | 5.396 | 67968
9 | 12 | 高 | 45 | 仅风机盘管 | [6 empty] | 10:50 | 38.4 | 81.6 | 81.6 | 10:50 | 26.4 |  | 10:50 | 235.2 | 2.505 | 56448
10 | 最佳 | - | 45 | 仅地暖 | [6 empty] | 11:00 | 38.4 | 81.6 | 81.6 | 11:00 | 26.4 |  | 11:00 | 314.4 | 3.067 | 75456
11 | 最佳 | 低 | 45 | 风盘+地暖 | [6 empty] | 11:10 | 38.4 | 81.6 | 81.6 | 11:10 | 26.4 |  | 11:10 | 309.6 | 0.93 | 74304
12 | 最佳 | 中 | 45 | 风盘+地暖 | [6 empty] | 11:20 | 38.4 | 81.6 | 81.6 | 11:20 | 26.4 |  | 11:20 | 348 | 5.403 | 83520
13 | 最佳 | 高 | 45 | 风盘+地暖 | [6 empty] | 11:30 | 38.4 | 81.6 | 81.6 | 11:30 | 26.4 |  | 11:30 | 372 | 5.486 | 89280
14 | 最佳 | 低 | 35 | 仅风机盘管 | [6 empty] | 11:40 | 38.4 | 81.6 | 81.6 | 11:40 | 26.4 |  | 11:40 | 254.4 | 1.89 | 61056
15 | 最佳 | 中 | 35 | 仅风机盘管 | [6 empty] | 11:50 | 38.4 | 81.6 | 81.6 | 11:50 | 26.4 |  | 11:50 | 496.8 | 3.66 | 119232
16 | 最佳 | 高 | 35 | 仅风机盘管 | [6 empty] | 12:00 | 38.4 | 81.6 | 81.6 | 12:00 | 26.4 |  | 12:00 | 232.8 | 5.283 | 55872
17 | 最佳 | - | 35 | 仅地暖 | [6 empty] | 12:10 | 38.4 | 81.6 | 81.6 | 12:10 | 26.4 |  | 12:10 | 300 | 2.49 | 72000
18 | 最佳 | 低 | 35 | 风盘+地暖 | [6 empty] | 12:20 | 38.4 | 81.6 | 81.6 | 12:20 | 26.4 |  | 12:20 | 367.2 | 5.3 | 88128
19 | 最佳 | 中 | 35 | 风盘+地暖 | [6 empty] | 12:30 | 38.4 | 81.6 | 81.6 | 12:30 | 26.4 |  | 12:30 | 396 | 2.54 | 95040
20 | 最佳 | 高 | 35 | 风盘+地暖 | [6 empty] | 12:40 | 38.4 | 81.6 | 81.6 | 12:40 | 26.4 |  | 12:40 | 434.4 | 4.48 | 104256
21 | 最佳 | 低 | 55 | 仅风机盘管 | [6 empty] | 12:50 | 38.4 | 81.6 | 81.6 | 12:50 | 26.4 |  | 12:50 | 247.2 | 3.09 | 59328
22 | 最佳 | 中 | 55 | 仅风机盘管 | [6 empty] | 13:00 | 38.4 | 81.6 | 81.6 | 13:00 | 26.4 |  | 13:00 | 434.4 | 3.05 | 104256
23 | 最佳 | 高 | 55 | 仅风机盘管 | [6 empty] | 13:10 | 38.4 | 81.6 | 81.6 | 13:10 | 26.4 |  | 13:10 | 393.6 | 0.97 | 94464
24 | 最佳 | - | 55 | 仅地暖 | [6 empty] | 13:20 | 38.4 | 81.6 | 81.6 | 13:20 | 26.4 |  | 13:20 | 307.2 | 5.06 | 73728
25 | 最佳 | 低 | 55 | 风盘+地暖 | [6 empty] | 13:30 | 38.4 | 81.6 | 81.6 | 13:30 | 26.4 |  | 13:30 | 360 | 2.39 | 86400
26 | 最佳 | 中 | 55 | 风盘+地暖 | [6 empty] | 13:40 | 38.4 | 81.6 | 81.6 | 13:40 | 26.4 |  | 13:40 | 612 | 1.88 | 146880
27 | 最佳 | 高 | 55 | 风盘+地暖 | [6 empty] | 13:50 | 38.4 | 81.6 | 81.6 | 13:50 | 26.4 |  | 13:50 | 280.8 | 5.09 | 67392
[11 empty] | 14:00 | 38.4 | 81.6 | 81.6 | 14:00 | 26.4 |  | 14:00 | 254.4 | 1.91 | 61056
性能曲线名称 | 性能曲线函数表达式 | [9 empty] | 14:10 | 38.4 | 81.6 | 81.6 | 14:10 | 26.4 |  | 14:10 | 391.2 | 5.32 | 93888
CAP-T | [10 empty] | 14:20 | 38.4 | 81.6 | 81.6 | 14:20 | 26.4 |  | 14:20 | 381.6 | 2.49 | 91584
EIR-T | [10 empty] | 14:30 | 38.4 | 81.6 | 81.6 | 14:30 | 26.4 |  | 14:30 | 283.2 | 4.89 | 67968
EIR-PLR |  |  |  | 时间 | 模拟结果 | 实测结果 | 时间 | 室外温度 | 室外相对湿度 |  | 14:40 | 38.4 | 81.6 | 81.6 | 14:40 | 26.4 |  | 14:40 | 292.8 | 5.16 | 70272
9:15 | 31.2 | 77.3 |  | 1:00 | 27.602 | 26.7 | 9:15 | 31.2 | 77.3 |  | 14:50 | 38.4 | 81.6 | 81.6 | 14:50 | 26.4 |  | 14:50 | 252 | 1.28 | 60480
10:15 | 33.2 | 68 |  | 2:00 | 27.2347 | 26.5 | 10:15 | 32.2 | 72 |  | 15:00 | 38.4 | 81.6 | 81.6 | 15:00 | 26.4 |  | 15:00 | 348 | 5.01 | 83520
11:15 | 33 | 62 |  | 3:00 | 26.975 | 27.2 | 11:15 | 33 | 62 |  | 15:10 | 38.4 | 81.6 | 81.6 | 15:10 | 26.4 |  | 15:10 | 362.4 | 1.83 | 86976
12:15 | 31.2 | 71.4 |  | 4:00 | 26.747 | 26.9 | 12:15 | 31.2 | 71.4 |  | 15:20 | 38.4 | 81.6 | 81.6 | 15:20 | 26.4 |  | 15:20 | 343.2 | 4.18 | 82368
13:15 | 28.6 | 95.6 |  | 5:00 | 26.5633 | 27.6 | 13:15 | 32.1 | 75.6 |  | 15:30 | 38.4 | 81.6 | 81.6 | 15:30 | 26.4 |  | 15:30 | 417.6 | 5.27 | 100224
14:15 | 30.8 | 84.1 |  | 6:00 | 26.5887 | 28.1 | 14:15 | 34.1 | 69.1 |  | 15:40 | 38.4 | 81.6 | 81.6 | 15:40 | 26.4 |  | 15:40 | 302.4 | 1.07 | 72576
15:15 | 29.4 | 86.1 |  | 7:00 | 26.9623 | 28.5 | 15:15 | 32.7 | 86.1 | 室外相对湿+K40度+H33:J34 | 15:50 | 38.4 | 81.6 | 81.6 | 15:50 | 26.4 |  | 15:50 | 307.2 | 3.3 | 73728
16:15 | 28.4 | 90.2 |  | 8:00 | 27.9377 | 29.4 | 16:15 | 31.8 | 90.2 |  | 16:00 | 38.4 | 81.6 | 81.6 | 16:00 | 26.4 |  | 16:00 | 477.6 | 4.11 | 114624
17:15 | 28.8 | 85 |  | 9:00 | 29.3183 | 31.2 | 17:15 | 30.5 | 95.3 |  | 16:10 | 38.4 | 81.6 | 81.6 | 16:10 | 26.4 |  | 16:10 | 345.6 | 0.93 | 82944
18:15 | 28 | 87 |  | 10:00 | 30.6737 | 32.2 | 18:15 | 29.6 | 95.1 |  | 16:20 | 38.4 | 81.6 | 81.6 | 16:20 | 26.4 |  | 16:20 | 367.2 | 0.95 | 88128
19:15 | 27.2 | 88.7 |  | 11:00 | 31.877 | 33 | 19:15 | 29.3 | 88.7 |  | 16:30 | 38.4 | 81.6 | 81.6 | 16:30 | 26.4 |  | 16:30 | 261.6 | 5.26 | 62784
20:15 | 27 | 87.2 |  | 12:00 | 32.7953 | 31.2 | 20:15 | 28 | 92.2 |  | 16:40 | 38.4 | 81.6 | 81.6 | 16:40 | 26.4 |  | 16:40 | 247.2 | 1.81 | 59328
21:15 | 27.2 | 84.6 |  | 13:00 | 33.4667 | 32.1 | 21:15 | 27.2 | 88.6 |  | 16:50 | 38.4 | 81.6 | 81.6 | 16:50 | 26.4 |  | 16:50 | 319.2 | 3 | 76608
22:15 |  |  |  | 14:00 | 33.9417 | 34.1 | 22:15 | 27.2 | 69.8 |  | 17:00 | 38.4 | 81.6 | 81.6 | 17:00 | 26.4 |  | 17:00 | 523.2 | 3.42 | 125568
23:15 |  |  |  | 15:00 | 34.1 | 32.7 | 23:15 | 26.9 | 82.1 |  | 17:10 | 38.4 | 81.6 | 81.6 | 17:10 | 26.4 |  | 17:10 | 376.8 | 2.1 | 90432
24:15 |  |  |  | 16:00 | 33.834 | 31.8 | 24:15 | 27 | 73.4 |  | 17:20 | 38.4 | 81.6 | 81.6 | 17:20 | 26.4 |  | 17:20 | 357.6 | 4.39 | 85824
25:15 | 26.7 | 85.7 |  | 17:00 | 33.2893 | 30.5 | 25:15 | 26.7 | 85.7 |  | 17:30 | 38.4 | 81.6 | 81.6 | 17:30 | 26.4 |  | 17:30 | 391.2 | 5.18 | 93888
26:15 | 26.5 | 87.5 |  | 18:00 | 32.5927 | 29.6 | 26:15 | 26.5 | 87.5 |  | 17:40 | 38.4 | 81.6 | 81.6 | 17:40 | 26.4 |  | 17:40 | 278.4 | 1.87 | 66816
27:15 | 26.4 | 91.3 |  | 19:00 | 31.611 | 29.3 | 27:15 | 27.2 | 79.3 |  | 17:50 | 38.4 | 81.6 | 81.6 | 17:50 | 26.4 |  | 17:50 | 300 | 3.44 | 72000
28:15 | 26.9 | 90.1 |  | 20:00 | 30.6483 | 28 | 28:15 | 26.9 | 84.1 |  | 18:00 | 38.4 | 81.6 | 81.6 | 18:00 | 26.4 |  | 18:00 | 492 | 4.25 | 118080
29:15 | 26.1 | 90.6 |  | 21:00 | 29.901 | 27.2 | 29:15 | 27.6 | 80.6 |  | 18:10 | 38.4 | 81.6 | 81.6 | 18:10 | 26.4 |  | 18:10 | 367.2 | 2 | 88128
30:15 | 25.3 | 91.3 |  | 22:00 | 29.217 | 27.2 | 30:15 | 28.1 | 78.3 |  | 18:20 | 38.4 | 81.6 | 81.6 | 18:20 | 26.4 |  | 18:20 | 355.2 | 2.41 | 85248
31:15 | 25.1 | 92.9 |  | 23:00 | 28.6217 | 26.9 | 31:15 | 28.5 | 72.9 |  | 18:30 | 38.4 | 81.6 | 81.6 | 18:30 | 26.4 |  | 18:30 | 302.4 | 5 | 72576
32:15 | 25.4 | 91.4 |  | 24:00 | 28.0897 | 27 | 32:15 | 29.4 | 71.4 |  | 18:40 | 38.4 | 81.6 | 81.6 | 18:40 | 26.4 |  | 18:40 | 283.2 | 2.08 | 67968
33:15 | 25.8 | 88.2 | [8 empty] | 18:50 | 38.4 | 81.6 | 81.6 | 18:50 | 26.4 |  | 18:50 | 364.8 | 1.91 | 87552
[6 empty] | -1.3667 |  |  |  |  | 19:00 | 38.4 | 81.6 | 81.6 | 19:00 | 26.4 |  | 19:00 | 324 | 0.92 | 77760
[6 empty] | 0.15833 | 室内温度设定值（℃） | 26 |  |  | 19:10 | 38.4 | 81.6 | 81.6 | 19:10 | 26.4 |  | 19:10 | 292.8 | 5.07 | 70272
[6 empty] | -1.4 | 新风风量（） | 350 |  |  | 19:20 | 38.4 | 81.6 | 81.6 | 19:20 | 26.4 |  | 19:20 | 348 | 2.91 | 83520
[6 empty] | -2.034 | 热泵主机供水温度（℃） | 10 |  |  | 19:30 | 38.4 | 81.6 | 81.6 | 19:30 | 26.4 |  | 19:30 | 340.8 | 5.54 | 81792
[6 empty] | -2.7893 | 风机盘管运行档位 | 中 |  |  | 19:40 | 38.4 | 81.6 | 81.6 | 19:40 | 26.4 |  | 19:40 | 283.2 | 1.08 | 67968
[6 empty] | -2.9927 |  |  |  |  | 19:50 | 38.4 | 81.6 | 81.6 | 19:50 | 26.4 |  | 19:50 | 314.4 | 3.16 | 75456
[6 empty] | -2.311 |  |  |  |  | 20:00 | 38.4 | 81.6 | 81.6 | 20:00 | 26.4 |  | 20:00 | 331.2 | 2.87 | 79488
[6 empty] | -2.6483 |  |  |  |  | 20:10 | 38.4 | 81.6 | 81.6 | 20:10 | 26.4 |  | 20:10 | 540 | 2.53 | 129600
[5 empty] | Whole Building:Facility Total Purchased Electricity Energy [J](Hourly) | -2.701 |  |  |  |  | 20:20 | 38.4 | 81.6 | 81.6 | 20:20 | 26.4 |  | 20:20 | 364.8 | 4.39 | 87552
[5 empty] | 6462849.8537 | -2.017 | 1.7952 | 2.244 | 2.31 | 0.065955 | 20:30 | 38.4 | 81.6 | 81.6 | 20:30 | 26.4 |  | 20:30 | 328.8 | 4.05 | 78912
[5 empty] | 6386736.645 | -1.7217 | 1.7741 | 2.2176 | 2.35 | 0.13238 | 20:40 | 38.4 | 81.6 | 81.6 | 20:40 | 26.4 |  | 20:40 | 396 | 5.06 | 95040
[5 empty] | 6333087.724 | -1.0897 | 1.7592 | 2.199 | 2.16 | -0.038989 | 20:50 | 38.4 | 81.6 | 81.6 | 20:50 | 26.4 |  | 20:50 | 340.8 | 2.34 | 81792
[5 empty] | 6286202.7204 |  | 1.7462 | 2.1827 | 2.23 | 0.047291 | 21:00 | 38.4 | 81.6 | 81.6 | 21:00 | 26.4 |  | 21:00 | 295.2 | 2.21 | 70848
[5 empty] | 6248575.4871 |  | 1.7357 | 2.1696 | 2.22 | 0.050356 | 21:10 | 38.4 | 81.6 | 81.6 | 21:10 | 26.4 |  | 21:10 | 259.2 | 2.71 | 62208
[5 empty] | 6253743.8249 |  | 1.7372 | 2.1714 | 2.21 | 0.038561 | 21:20 | 38.4 | 81.6 | 81.6 | 21:20 | 26.4 |  | 21:20 | 297.6 | 3.86 | 71424
[5 empty] | 6330473.9354 |  | 1.7585 | 2.1981 | 2.131 | -0.067081 | 21:30 | 38.4 | 81.6 | 81.6 | 21:30 | 26.4 |  | 21:30 | 261.6 | 0.86 | 62784
[5 empty] | 5962733.4385 |  | 1.6563 | 2.0704 | 2.01 | -0.060394 | 21:40 | 38.4 | 81.6 | 81.6 | 21:40 | 26.4 |  | 21:40 | 244.8 | 3.08 | 58752
[5 empty] | 6263125.0882 |  | 1.7398 | 2.1747 | 2.1 | -0.074696 | 21:50 | 38.4 | 81.6 | 81.6 | 21:50 | 26.4 |  | 21:50 | 518.4 | 2.77 | 124416
[5 empty] | 6557046.2476 |  | 1.8214 | 2.2768 | 2.22 | -0.056752 | 22:00 | 38.4 | 81.6 | 81.6 | 22:00 | 26.4 |  | 22:00 | 288 | 2.06 | 69120
[5 empty] | 6833891.5309 |  | 1.8983 | 2.3729 | 2.45 | 0.077121 | 22:10 | 38.4 | 81.6 | 81.6 | 22:10 | 26.4 |  | 22:10 | 328.8 | 2 | 78912
[5 empty] | 7052409.4808 |  | 1.959 | 2.4488 | 2.45 | 0.0012467 | 22:20 | 38.4 | 81.6 | 81.6 | 22:20 | 26.4 |  | 22:20 | 273.6 | 4.89 | 65664
[5 empty] | 7182314.5003 |  | 1.9951 | 2.4939 | 2.63 | 0.13614 | 22:30 | 38.4 | 81.6 | 81.6 | 22:30 | 26.4 |  | 22:30 | 324 | 2.36 | 77760
[5 empty] | 7206541.315 |  | 2.0018 | 2.5023 | 2.66 | 0.15773 | 22:40 | 38.4 | 81.6 | 81.6 | 22:40 | 26.4 |  | 22:40 | 355.2 | 2.37 | 85248
[5 empty] | 7213964.9721 |  | 2.0039 | 2.5048 | 2.43 | -0.074849 | 22:50 | 38.4 | 81.6 | 81.6 | 22:50 | 26.4 |  | 22:50 | 314.4 | 3.73 | 75456
[5 empty] | 7201502.816 |  | 2.0004 | 2.5005 | 2.55 | 0.049478 | 23:00 | 38.4 | 81.6 | 81.6 | 23:00 | 26.4 |  | 23:00 | 319.2 | 0.97 | 76608
[5 empty] | 7150786.0831 |  | 1.9863 | 2.4829 | 2.49 | 0.0070882 | 23:10 | 38.4 | 81.6 | 81.6 | 23:10 | 26.4 |  | 23:10 | 314.4 | 0.91 | 75456
[5 empty] | 6991215.6896 |  | 1.942 | 2.4275 | 2.46 | 0.032495 | 23:20 | 38.4 | 81.6 | 81.6 | 23:20 | 26.4 |  | 23:20 | 280.8 | 0.91 | 67392
[5 empty] | 7333747.0096 |  | 2.0372 | 2.5464 | 2.49 | -0.05644 | 23:30 | 38.4 | 81.6 | 81.6 | 23:30 | 26.4 |  | 23:30 | 242.4 | 5.1 | 58176
[5 empty] | 7114242.7368 |  | 1.9762 | 2.4702 | 2.4 | -0.070223 | 23:40 | 38.4 | 81.6 | 81.6 | 23:40 | 26.4 |  | 23:40 | 338.4 | 2.3 | 81216
[5 empty] | 6951698.8821 |  | 1.931 | 2.4138 | 2.33 | -0.083784 | 23:50 | 38.4 | 81.6 | 81.6 | 23:50 | 26.4 |  | 23:50 | 340.8 | 1.67 | 81792
[5 empty] | 6804447.1756 |  | 1.8901 | 2.3627 | 2.35 | -0.012655 | 24:00 | 38.4 | 81.6 | 81.6 | 24:00 | 26.4 |  | 24:00 | 290.4 | 4.88 | 69696
[5 empty] | 6677449.7654 |  | 1.8548 | 2.3186 | 2.38 | 0.061441 | 24:10 | 38.4 | 81.6 | 81.6 | 24:10 | 26.4 |  | 24:10 | 276 | 3.19 | 66240
[5 empty] | 6565003.6765 |  | 1.8236 | 2.2795 | 2.33 | 0.050485 | 24:20 | 38.4 | 81.6 | 81.6 | 24:20 | 26.4 |  | 24:20 | 254.4 | 2.84 | 61056
[10 empty] | 0.012996 | 24:30 | 38.4 | 81.6 | 81.6 | 24:30 | 26.4 |  | 24:30 | 482.4 | 3.07 | 115776
[11 empty] | 24:40 | 38.4 | 81.6 | 81.6 | 24:40 | 26.4 |  | 24:40 | 295.2 | 0.88 | 70848
[11 empty] | 24:50 | 38.4 | 81.6 | 81.6 | 24:50 | 26.4 |  | 24:50 | 280.8 | 0.89 | 67392
[11 empty] | 25:00 | 38.4 | 81.6 | 81.6 | 25:00 | 26.4 |  | 25:00 | 230.4 | 2 | 55296
[6 empty] | 9:15 | 10:15 | 9:15~10:15 | 2.22 | 2.31 | 25:10 | 38.4 | 81.6 | 81.6 | 25:10 | 26.4 |  | 25:10 | 518.4 | 2.54 | 124416
[6 empty] | 10:15 | 11:15 | 10:15~11:15 | 2.45 | 2.35 | 25:20 | 38.4 | 81.6 | 81.6 | 25:20 | 26.4 |  | 25:20 | 348 | 2.28 | 83520
[6 empty] | 11:15 | 12:15 | 11:15~12:15 | 2.45 | 2.16 | 25:30 | 38.4 | 81.6 | 81.6 | 25:30 | 26.4 |  | 25:30 | 331.2 | 1.74 | 79488
[6 empty] | 12:15 | 13:15 | 12:15~13:15 | 2.63 | 2.23 | 25:40 | 38.4 | 81.6 | 81.6 | 25:40 | 26.4 |  | 25:40 | 254.4 | 4.78 | 61056
[6 empty] | 13:15 | 14:15 | 13:15~14:15 | 2.43 | 2.22 | 25:50 | 38.4 | 81.6 | 81.6 | 25:50 | 26.4 |  | 25:50 | 264 | 2.98 | 63360
[6 empty] | 14:15 | 15:15 | 14:15~15:15 | 2.66 | 2.21 | 26:00 | 38.4 | 81.6 | 81.6 | 26:00 | 26.4 |  | 26:00 | 292.8 | 2.25 | 70272
[6 empty] | 15:15 | 16:15 | 15:15~16:15 | 2.55 | 2.131 | 26:10 | 38.4 | 81.6 | 81.6 | 26:10 | 26.4 |  | 26:10 | 357.6 | 2.27 | 85824
[6 empty] | 16:15 | 17:15 | 16:15~17:15 | 2.49 | 2.01 | 26:20 | 38.4 | 81.6 | 81.6 | 26:20 | 26.4 |  | 26:20 | 304.8 | 0.2 | 73152
[6 empty] | 17:15 | 18:15 | 17:15~18:15 | 2.46 | 2.1 | 26:30 | 38.4 | 81.6 | 81.6 | 26:30 | 26.4 |  | 26:30 | 297.6 | 0.9 | 71424
[6 empty] | 18:15 | 19:15 | 18:15~19:15 | 2.49 | 2.22 | 26:40 | 38.4 | 81.6 | 81.6 | 26:40 | 26.4 |  | 26:40 | 324 | 4.06 | 77760
[6 empty] | 19:15 | 20:15 | 19:15~20:15 | 2.4 | 2.45 | 26:50 | 38.4 | 81.6 | 81.6 | 26:50 | 26.4 |  | 26:50 | 331.2 | 4.7 | 79488
[6 empty] | 20:15 | 21:15 | 20:15~21:15 | 2.33 | 2.45 | 27:00 | 38.4 | 81.6 | 81.6 | 27:00 | 26.4 |  | 27:00 | 324 | 2.25 | 77760
[6 empty] | 21:15 | 22:15 | 21:15~22:15 | 2.35 | 2.63 | 27:10 | 38.4 | 81.6 | 81.6 | 27:10 | 26.4 |  | 27:10 | 319.2 | 2.26 | 76608
[6 empty] | 22:15 | 23:15 | 22:15~23:15 | 2.38 | 2.66 | 27:20 | 38.4 | 81.6 | 81.6 | 27:20 | 26.4 |  | 27:20 | 448.8 | 2.28 | 107712
[6 empty] | 23:15 | 24:15 | 23:15~0:15 | 2.33 | 2.43 | 27:30 | 38.4 | 81.6 | 81.6 | 27:30 | 26.4 |  | 27:30 | 290.4 | 0.89 | 69696
[6 empty] | 24:15 | 25:15 | 0:15~1:15 | 2.31 | 2.55 | 27:40 | 38.4 | 81.6 | 81.6 | 27:40 | 26.4 |  | 27:40 | 297.6 | 0.89 | 71424
[6 empty] | 25:15 | 26:15 | 1:15~2:15 | 2.25 | 2.49 | 27:50 | 38.4 | 81.6 | 81.6 | 27:50 | 26.4 |  | 27:50 | 240 | 1.76 | 57600
[6 empty] | 26:15 | 27:15 | 2:15~3:15 | 2.16 | 2.46 | 28:00 | 38.4 | 81.6 | 81.6 | 28:00 | 26.4 |  | 28:00 | 232.8 | 3.44 | 55872
[6 empty] | 27:15 | 28:15 | 3:15~4:15 | 2.23 | 2.49 | 28:10 | 38.4 | 81.6 | 81.6 | 28:10 | 26.4 |  | 28:10 | 314.4 | 2.51 | 75456
[6 empty] | 28:15 | 29:15 | 4:15~5:15 | 2.22 | 2.4 | 28:20 | 38.4 | 81.6 | 81.6 | 28:20 | 26.4 |  | 28:20 | 302.4 | 2.22 | 72576
[6 empty] | 29:15 | 30:15 | 5:15~6:15 | 2.21 | 2.33 | 28:30 | 38.4 | 81.6 | 81.6 | 28:30 | 26.4 |  | 28:30 | 537.6 | 2.45 | 129024
[6 empty] | 30:15 | 31:15 | 6:15~7:15 | 2.131 | 2.35 | 28:40 | 38.4 | 81.6 | 81.6 | 28:40 | 26.4 |  | 28:40 | 362.4 | 0.89 | 86976
[6 empty] | 31:15 | 32:15 | 7:15~8:15 | 2.01 | 2.38 | 28:50 | 38.4 | 81.6 | 81.6 | 28:50 | 26.4 |  | 28:50 | 285.6 | 0.89 | 68544
[6 empty] | 32:15 | 33:15 | 8:15~9:15 | 2.1 | 2.33 | 29:00 | 38.4 | 81.6 | 81.6 | 29:00 | 26.4 |  | 29:00 | 324 | 3.57 | 77760
[11 empty] | 29:10 | 38.4 | 81.6 | 81.6 | 29:10 | 26.4 |  | 29:10 | 252 | 3.67 | 60480
|  |  | ExprDay1, !- Name 8, !- Month 30, !- Day of Month Wednesday, !- Day Type 34.1, !- Maximum Dry-Bulb Temperature {C} 6, !- Daily Dry-Bulb Temperature Range {deltaC} , !- Dry-Bulb Temperature Range Modifier Type , !- Dry-Bulb Temperature Range Modifier Day Schedule Name WetBulb, !- Humidity Condition Type 26.5, !- Wetbulb or DewPoint at Maximum Dry-Bulb {C} , !- Humidity Condition Day Schedule Name , !- Humidity Ratio at Maximum Dry-Bulb {kgWater/kgDryAir} , !- Enthalpy at Maximum Dry-Bulb {J/kg} , !- Daily Wet-Bulb Temperature Range {deltaC} 101259, !- Barometric Pressure {Pa} 3.6, !- Wind Speed {m/s} 250, !- Wind Direction {deg} No, !- Rain Indicator No, !- Snow Indicator No, !- Daylight Saving Time Indicator ASHRAETau, !- Solar Model Indicator , !- Beam Solar Day Schedule Name , !- Diffuse Solar Day Schedule Name 0.882, !- ASHRAE Clear Sky Optical Depth for Beam Irradiance (taub) {dimensionless} 1.308, !- ASHRAE Clear Sky Optical Depth for Diffuse Irradiance (taud) {dimensionless} , !- Sky Clearness , !- Maximum Number Warmup Days | [7 empty] | 29:20 | 38.4 | 81.6 | 81.6 | 29:20 | 26.4 |  | 29:20 | 276 | 2.33 | 66240
[11 empty] | 29:30 | 38.4 | 81.6 | 81.6 | 29:30 | 26.4 |  | 29:30 | 271.2 | 2.19 | 65088
[11 empty] | 29:40 | 38.4 | 81.6 | 81.6 | 29:40 | 26.4 |  | 29:40 | 319.2 | 2.76 | 76608
[11 empty] | 29:50 | 38.4 | 81.6 | 81.6 | 29:50 | 26.4 |  | 29:50 | 343.2 | 0.99 | 82368
[7 empty] | 日期 | 2023-08-30 |  |  | 30:00 | 38.4 | 81.6 | 81.6 | 30:00 | 26.4 |  | 30:00 | 338.4 | 1.66 | 81216
[7 empty] | 室外空气最大干球温度（℃） | 34.1 |  |  | 30:10 | 38.4 | 81.6 | 81.6 | 30:10 | 26.4 |  | 30:10 | 259.2 | 0.87 | 62208
[7 empty] | 该日干球温度波动幅度（℃） | 7.6 |  |  | 30:20 | 38.4 | 81.6 | 81.6 | 30:20 | 26.4 |  | 30:20 | 396 | 4.97 | 95040
[7 empty] | 最大干球温度时的湿球温度（℃） | 29.02 |  |  | 30:30 | 38.4 | 81.6 | 81.6 | 30:30 | 26.4 |  | 30:30 | 259.2 | 2.3 | 62208
[7 empty] | 大气压力（Pa） | 101259 |  |  | 30:40 | 38.4 | 81.6 | 81.6 | 30:40 | 26.4 |  | 30:40 | 302.4 | 2.21 | 72576
[7 empty] | 风速（m/s） | 3.6 |  |  | 30:50 | 38.4 | 81.6 | 81.6 | 30:50 | 26.4 |  | 30:50 | 448.8 | 2.24 | 107712
[7 empty] | 风向 | 250° |  |  | 31:00 | 38.4 | 81.6 | 81.6 | 31:00 | 26.4 |  | 31:00 | 328.8 | 1.13 | 78912
[11 empty] | 31:10 | 38.4 | 81.6 | 81.6 | 31:10 | 26.4 |  | 31:10 | 316.8 | 0.93 | 76032
[11 empty] | 31:20 | 38.4 | 81.6 | 81.6 | 31:20 | 26.4 |  | 31:20 | 297.6 | 0.9 | 71424
[11 empty] | 31:30 | 38.4 | 81.6 | 81.6 | 31:30 | 26.4 |  | 31:30 | 280.8 | 4.38 | 67392
[11 empty] | 31:40 | 38.4 | 81.6 | 81.6 | 31:40 | 26.4 |  | 31:40 | 273.6 | 2.7 | 65664
[11 empty] | 31:50 | 38.4 | 81.6 | 81.6 | 31:50 | 26.4 |  | 31:50 | 292.8 | 2.22 | 70272
[11 empty] | 32:00 | 38.4 | 81.6 | 81.6 | 32:00 | 26.4 |  | 32:00 | 319.2 | 2.21 | 76608
[11 empty] | 32:10 | 38.4 | 81.6 | 81.6 | 32:10 | 26.4 |  | 32:10 | 312 | 0.9 | 74880
[11 empty] | 32:20 | 38.4 | 81.6 | 81.6 | 32:20 | 26.4 |  | 32:20 | 264 | 0.86 | 63360
[11 empty] | 32:30 | 38.4 | 81.6 | 81.6 | 32:30 | 26.4 |  | 32:30 | 249.6 | 2.15 | 59904
[11 empty] | 32:40 | 38.4 | 81.6 | 81.6 | 32:40 | 26.4 |  | 32:40 | 333.6 | 2.2 | 80064
[11 empty] | 32:50 | 38.4 | 81.6 | 81.6 | 32:50 | 26.4 |  | 32:50 | 338.4 | 0.98 | 81216
[11 empty] | 33:00 | 38.4 | 81.6 | 81.6 | 33:00 | 26.4 |  | 33:00 | 300 | 0.91 | 72000
[11 empty] | 33:10 | 38.4 | 81.6 | 81.6 | 33:10 | 26.4 |  | 33:10 | 268.8 | 2.87 | 64512
[14 empty] | 实测数据 | 模拟数据
[6 empty] | 时间 | 室外温度（℃） |  | 时间段 | 系统每小时耗能（kW） | 室外温度（℃） |  | 0:00~1:00 | 2.31 | 2.244 |  | 9:15~10:15 | 2.22
[6 empty] | 9:15 | 31.2 |  | 9:15~10:15 | 2.22 | 31.2 |  | 1:00~2:00 | 2.25 | 2.2176 |  | 10:15~11:15 | 2.45
[6 empty] | 10:15 | 32.2 |  | 10:15~11:15 | 2.45 | 32.2 |  | 2:00~3:00 | 2.16 | 2.199 |  | 11:15~12:15 | 2.45
[6 empty] | 11:15 | 33 |  | 11:15~12:15 | 2.45 | 33 |  | 3:00~4:00 | 2.23 | 2.1827 |  | 12:15~13:15 | 2.63
[6 empty] | 12:15 | 31.2 |  | 12:15~13:15 | 2.63 | 31.2 |  | 4:00~5:00 | 2.22 | 2.1696 |  | 13:15~14:15 | 2.43
[6 empty] | 13:15 | 32.1 |  | 13:15~14:15 | 2.43 | 32.1 |  | 5:00~6:00 | 2.21 | 2.1714 |  | 14:15~15:15 | 2.66
[6 empty] | 14:15 | 34.1 |  | 14:15~15:15 | 2.66 | 34.1 |  | 6:00~7:00 | 2.131 | 2.1981 |  | 15:15~16:15 | 2.55
[6 empty] | 15:15 | 32.7 |  | 15:15~16:15 | 2.55 | 32.7 |  | 7:00~8:00 | 2.01 | 2.0704 |  | 16:15~17:15 | 2.49
[6 empty] | 16:15 | 31.8 |  | 16:15~17:15 | 2.49 | 31.8 |  | 8:00~9:00 | 2.1 | 2.1747 |  | 17:15~18:15 | 2.46
[6 empty] | 17:15 | 30.5 |  | 17:15~18:15 | 2.46 | 30.5 |  | 9:00~10:00 | 2.22 | 2.2768 |  | 18:15~19:15 | 2.49
[6 empty] | 18:15 | 29.6 |  | 18:15~19:15 | 2.49 | 29.6 |  | 10:00~11:00 | 2.45 | 2.3729 |  | 19:15~20:15 | 2.4
[6 empty] | 19:15 | 29.3 |  | 19:15~20:15 | 2.4 | 29.3 |  | 11:00~12:00 | 2.45 | 2.4488 |  | 20:15~21:15 | 2.33
[6 empty] | 20:15 | 28 |  | 20:15~21:15 | 2.33 | 28 |  | 12:00~13:00 | 2.63 | 2.4939 |  | 21:15~22:15 | 2.35
[6 empty] | 21:15 | 27.2 |  | 21:15~22:15 | 2.35 | 27.2 |  | 13:00~14:00 | 2.43 | 2.5023 |  | 22:15~23:15 | 2.38
[6 empty] | 22:15 | 27.2 |  | 22:15~23:15 | 2.38 | 27.2 |  | 14:00~15::00 | 2.66 | 2.5048 |  | 23:15~0:15 | 2.33
[6 empty] | 23:15 | 26.9 |  | 23:15~0:15 | 2.33 | 26.9 |  | 15:00~16:00 | 2.55 | 2.5005 |  | 0:15~1:15 | 2.31
[6 empty] | 24:15 | 27 |  | 0:15~1:15 | 2.31 | 27 |  | 16:00~17:00 | 2.49 | 2.4829 |  | 1:15~2:15 | 2.25
[6 empty] | 25:15 | 26.7 |  | 1:15~2:15 | 2.25 | 26.7 |  | 17:00~18:00 | 2.46 | 2.4275 |  | 2:15~3:15 | 2.16
[6 empty] | 26:15 | 26.5 |  | 2:15~3:15 | 2.16 | 26.5 |  | 18:00~19:00 | 2.49 | 2.5464 |  | 3:15~4:15 | 2.23
[6 empty] | 27:15 | 27.2 |  | 3:15~4:15 | 2.23 | 27.2 |  | 19:00~20:00 | 2.4 | 2.4702 |  | 4:15~5:15 | 2.22
[6 empty] | 28:15 | 26.9 |  | 4:15~5:15 | 2.22 | 26.9 |  | 20:00~21:00 | 2.33 | 2.4138 |  | 5:15~6:15 | 2.21
[6 empty] | 29:15 | 27.6 |  | 5:15~6:15 | 2.21 | 27.6 |  | 21:00~22:00 | 2.35 | 2.3627 |  | 6:15~7:15 | 2.131
[6 empty] | 30:15 | 28.1 |  | 6:15~7:15 | 2.131 | 28.1 |  | 22:00~23:00 | 2.38 | 2.3186 |  | 7:15~8:15 | 2.01
[6 empty] | 31:15 | 28.5 |  | 7:15~8:15 | 2.01 | 28.5 |  | 23:00~0:00 | 2.33 | 2.2795 |  | 8:15~9:15 | 2.1
[6 empty] | 32:15 | 29.4 |  | 8:15~9:15 | 2.1 | 29.4 |  |  | 56.241 | 56.0291

## winter
气温
|  | 模拟 | 实测 | 相对湿度
| 1:00 | -2.375 | -2 | 43.3 | 48.3281
| 2:00 | -2.6167 | -2.2 | 46.2 | 49.4481
| 3:00 | -2.7875 | -2.6 | 47.9 | 50.2559
| 4:00 | -2.9375 | -3.1 | 46.5 | 50.9764
| 5:00 | -3.0583 | -2.8 | 43.6 | 51.5642
| 6:00 | -3.0417 | -2.5 | 43.3 | 51.4827
| 7:00 | -2.7958 | -1.6 | 39.7 | 50.2975
| 8:00 | -2.1542 | -1.7 | 40.9 | 47.3373
| 9:00 | -1.2458 | -1 | 35.5 | 43.4338
| 10:00 | -0.35417 | -0.2 | 35.9 | 39.9116
| 11:00 | 0.4375 | 0.5 | 33.3 | 37.1778
| 12:00 | 1.0417 | 1 | 35.3 | 35.3127
| 13:00 | 1.4833 | 1.3 | 36.3 | 34.01
| 14:00 | 1.7958 | 1.9 | 32.6 | 33.1171
| 15:00 | 1.9 | 1.9 | 32.8243 | 32.8243
| 16:00 | 1.725 | 1.6 | 29.9 | 33.3174
| 17:00 | 1.3667 | 1.3 | 33.1 | 34.3492
| 18:00 | 0.90833 | 1 | 35 | 35.7154
| 19:00 | 0.2625 | 0.7 | 38.2 | 37.7389
| 20:00 | -0.37083 | 0.1 | 38.4 | 39.9685
| 21:00 | -0.8625 | -0.8 | 43.5 | 41.8733
| 22:00 | -1.3125 | -1.2 | 43.6 | 43.6979
| 23:00 | -1.7042 | -2 | 47.1 | 45.3497
| 24:00 | -2.0542 | -1.9 | 47.3 | 46.8801
|  |  |  | 室外气温 | 系统每小时能耗
0:00 | 1:00 | 0:00 | 1:00 | -2 | 5.9 | 2.1439 | 7718071.6135
1:00 | 2:00 | 1:00 | 2:00 | -2.2 | 6.2 | 2.1554 | 7759285.6113
2:00 | 3:00 | 2:00 | 3:00 | -2.6 | 6.25 | 2.1639 | 7789994.9518
3:00 | 4:00 | 3:00 | 4:00 | -3.1 | 6.4 | 2.1715 | 7817300.2558
4:00 | 5:00 | 4:00 | 5:00 | -2.8 | 6.47 | 2.1779 | 7840537.8811
5:00 | 6:00 | 5:00 | 6:00 | -2.5 | 6.5 | 2.1791 | 7844771.2196
6:00 | 7:00 | 6:00 | 7:00 | -1.6 | 6.43 | 2.1712 | 7816226.4233
7:00 | 8:00 | 7:00 | 8:00 | -1.7 | 6.24 | 2.0071 | 7225709.9464
8:00 | 9:00 | 8:00 | 9:00 | -1 | 5.4 | 1.9075 | 6866996.889
9:00 | 10:00 | 9:00 | 10:00 | -0.2 | 5.37 | 1.864 | 6710280.8341
10:00 | 11:00 | 10:00 | 11:00 | 0.5 | 5.42 | 1.8243 | 6567456.8394
11:00 | 12:00 | 11:00 | 12:00 | 1 | 5.4 | 1.7883 | 6438035.1881
12:00 | 13:00 | 12:00 | 13:00 | 1.3 | 5.43 | 1.8223 | 6560126.9392
13:00 | 14:00 | 13:00 | 14:00 | 1.9 | 5.25 | 1.7459 | 6285352.2279
14:00 | 15:00 | 14:00 | 15:00 | 1.9 | 5.31 | 1.7351 | 6246381.0884
15:00 | 16:00 | 15:00 | 16:00 | 1.6 | 5.22 | 1.7415 | 6269264.7462
16:00 | 17:00 | 16:00 | 17:00 | 1.3 | 5.33 | 1.7581 | 6329266.7542
17:00 | 18:00 | 17:00 | 18:00 | 1 | 5.44 | 1.8558 | 6680785.1075
18:00 | 19:00 | 18:00 | 19:00 | 0.7 | 5.97 | 2.0244 | 7287857.6372
19:00 | 20:00 | 19:00 | 20:00 | 0.1 | 6.11 | 2.0509 | 7383303.6739
20:00 | 21:00 | 20:00 | 21:00 | -0.8 | 6.31 | 2.0717 | 7458147.4712
21:00 | 22:00 | 21:00 | 22:00 | -1.2 | 6.42 | 2.091 | 7527467.4925
22:00 | 23:00 | 22:00 | 23:00 | -2 | 6.4 | 2.1169 | 7620663.4753
23:00 | 24:00 | 23:00 | 24:00 | -1.9 | 6.44 | 2.1331 | 7679304.6705
5.22
6.5
0:20 | 1.02 |  |  |  | 5.9004
0:40 | 3.78 |  |  |  | 141.61
1:00 | 5.96
1:20 | 6.53
1:40 | 6.08
2:00 | 6.0888
2:20 | 6.336
2:40 | 6.438
3:00 | 6.1796
3:20 | 6.4388
3:40 | 6.3097
4:00 | 6.6845
4:20 | 6.0919
4:40 | 5.8705
5:00 | 5.6255
5:20 | 6.0888
5:40 | 5.5931
6:00 | 5.3432
6:20 | 5.5824
6:40 | 5.7684
7:00 | 6.1808
7:20 | 5.3293
7:40 | 5.8438
8:00 | 5.9247
8:20 | 6.0987
8:40 | 6.213 |  |  |  | 模拟 | 实测
9:00 | 6.0052 |  |  | 0:00~1:00 | 6.4317 | 5.9
9:20 | 5.479 |  |  | 1:00~2:00 | 6.4661 | 6.2
9:40 | 5.072 |  |  | 2:00~3:00 | 6.4917 | 6.25
10:00 | 5.6354 |  |  | 3:00~4:00 | 6.5144 | 6.4
10:20 | 5.1782 |  |  | 4:00~5:00 | 6.5338 | 6.47
10:40 | 5.289 |  |  | 5:00~6:00 | 6.5373 | 6.5
11:00 | 5.21 |  |  | 6:00~7:00 | 6.5135 | 6.43
11:20 | 4.0511 |  |  | 7:00~8:00 | 6.0214 | 6.24
11:40 | 4.5429 |  |  | 8:00~9:00 | 5.7225 | 5.4
12:00 | 4.8894 |  |  | 9:00~10:00 | 5.5919 | 5.37
12:20 | 5.9643 |  |  | 10:00~11:00 | 5.4729 | 5.42
12:40 | 4.9513 |  |  | 11:00~12:00 | 5.365 | 5.4
13:00 | 5.0473 |  |  | 12:00~13:00 | 5.4668 | 5.43
13:20 | 5.6996 |  |  | 13:00~14:00 | 5.2378 | 5.25
13:40 | 5.0467 |  |  | 14:00~15:00 | 5.2053 | 5.31
14:00 | 4.71 |  |  | 15:00~16:00 | 5.2244 | 5.22
14:20 | 5.4025 |  |  | 16:00~17:00 | 5.2744 | 5.33
14:40 | 5.4166 |  |  | 17:00~18:00 | 5.5673 | 5.44
15:00 | 5.1461 |  |  | 18:00~19:00 | 6.0732 | 5.97
15:20 | 5.4094 |  |  | 19:00~20:00 | 6.1528 | 6.11
15:40 | 5.1174 |  |  | 20:00~21:00 | 6.2151 | 6.31
16:00 | 5.0394 |  |  | 21:00~22:00 | 6.2729 | 6.42
16:20 | 5.7126 |  |  | 22:00~23:00 | 6.3506 | 6.4
16:40 | 5.5225 |  |  | 23:00~0:00 | 6.3994 | 6.44
17:00 | 5.1787
17:20 | 5.8295
17:40 | 5.6477
18:00 | 5.5417
18:20 | 5.7731
18:40 | 5.9562
19:00 | 6.3047
19:20 | 6.3425
19:40 | 5.5934
20:00 | 5.6982
20:20 | 5.6037
20:40 | 5.8703
21:00 | 5.6003
21:20 | 5.9202
21:40 | 6.6008
22:00 | 6.0089
22:20 | 5.6798
22:40 | 5.8022
23:00 | 6.0929
23:20 | 6.2815
23:40 | 6.8187
24:00 | 6.1527