## README
Two energy systems were designed to achieve thermal energy balance through the exchange of heat and cold beween the vertical farm
and the buildings within the Westindische buurt in the Netherlands:
I) The centralised configuration: 4-pipe district heat network with a central HP. The centralised configuration makes use of a central HP that upgrades the LT
heat produced when cooling the VF, the buildings, and supermarkets to mid-temperature for space heating and domestic hot water applications.
The centralised HP connects to a 4-pipe DHN, including cold, ultra-low, low, and mid-temperatures. An ATES system is integrated to overcome timing issues between heat and cold production and demand.
II) The centralised configuration: 2-pipe district heat network with decentralised HPs. The decentralised configuration uses a 2-pipes DHN with individual HPs to generate mid-temperature heat from LT
waste heat derived from cooling the VF, supermarkets, and the buildings. The DHN consist of uLT and cold pipes. Similar to the centralised system, the ATES is integrated to overcome timing issues
between heat and cold production and demand.
This dataset is used to calculate the performance of both configurations including annual and daily electricity pattern and heat and cold profiles.
More information is found in the underlying publication.
CONTENT
VF_char | Description of vertical farm characteristics
VF_CDS | Cooling and dehumidification system of the vertical farm
VF_Cen | Vertical farm in centralised configuration
Cen_year | Year-round energy performance of the centralised configuration
Cen_daily | Daily energy performance of the centralised configuration
VF_Dec | Vertical farm in decentralised configuration
Dec_year | Year-round energy performance of the decentralised configuration
Dec_daily | Daily energy performance of the decentralised configuration

## VF_char
Energy characteristics VF (baseline)
Photoperiod (light)
Temperature supply | 24 | C | Blom et al., 2023
Temperature return | 26 | C | Blom et al., 2023
Light qualities
PPFD | 200 | μmol s-1 m-2 | Blom et al., 2023
Photoperiod | 16 | h | Blom et al., 2023
molar efficacy | 3.5 | μmol J−1 | Weidner et al., 2021
DLI | 11.52 | mol m-2 d-1
Energy use LED and heat production
Watt per m2 | 57.1429 | W m-2
LED usage | 333.7143 | kWh m-2 y-1
Heat dissipated LED | 90% |  | Blom et al., 2023
cooling loads based on LED light | 300.3429 | kWh m-2 y-1
Total cooling demands per m2 cultivation
Qcooling | 300.3429 | kWh m-2 y-1
Qcooling | 1081.2343 | MJ m-2 y-1
Qcooling | 51.4286 | J m-2 s-1 | year-round, during photoperiod (16h)
Dark period
Temperature supply | 23 | C | Graamans et al., 2018 (night temperature about 2C higher)
Temperature return | 23 | C | No sensible heating during night, confirmed no temp increase by homa (16-06)
Light qualities
PPFD | 0 | μmol s-1 m-2 | Blom et al., 2023
Photoperiod | 8 | h | Blom et al., 2023
molar efficacy | 3.5 | μmol J−1 | Weidner et al., 2021
DLI | 0 | mol m-2 d-1
Energy use LED and heat production
Watt per m2 | 0 | W m-2
LED usage | 0 | kWh m-2 y-1
Heat dissipated LED | 90% |  | Blom et al., 2023
cooling loads based on LED light | 0 | kWh m-2 y-1
Latent heat demand | 32.8 | J/s m-2 | Graamans et al., 2021, at t=23C
Total cooling demands per m2 cultivation
Qcooling | 95.776 | kWh m-2 y-1
Qcooling | 344.7936 | MJ m-2 y-1
Qcooling | 32.8 | J m-2 s-1 | year-round, during dark period (8h)

## VF_CDS
priniciple of cooling and re-heating
Dehumidification and cooling characteristics (per m2 cultivation)
Photoperiod (light)
PSYCHROMOMETRIC CHART PROPERTIES
Point 1 |  |  |  | Point 2 |  |  | Point 3
Temperature T1 | 26 | C |  | Temperature T2 | 19.511 | C | Temperature T3 | 24 | C
R.H. 1 | 72% |  |  | R.H. 2 | 100% |  | R.H. 3 | 76%
enthalphy h1 | 65.109 | kJ/kg |  | enthalphy h2 | 55.903 | kJ/kg | enthalphy h3 | 60.531 | kJ/kg
humidity ratio w 1 | 0.01529 | kg/kg |  | humidity ratio w2 | 0.014303 | kg/kg | humidity ratio w3 | 0.014303 | kg/kg
Specific volume v1 | 1.026 | m3/kg |  | Specific volume v2 | 0.848 | m3/kg | Specific volume v3 | 0.861 | m3/kg
Air density P1 | 1.169 | kg/m3 |  | Air density p2 | 1.196 | kg/m3 | Air density p3 | 1.178 | kg/m3
Specific heat Cpa 1 | 1026 | J/kg K |  |  |  |  | Specific heat Cpa 3 | 1025 | J/kg K
Qvertical farm produced (3->1)
Qtot = Qs + Ql | 0.051429 | kJ/s |  | latent and sensible heat as result of the LED
Qtot = ma * dh | 51.4286 | J m-2 s-1
Qs produced by light = Cpa * ma * dT | 0.024218 | kJ/s
Ql = ma * hw *dw =mw * hw | 0.027211 | kJ/s
ma (total for the VF) = Qtot / dh | 0.011234 | kg/s |  | during light hours of the VF (16h/d)
hwe latent heat evaporization water (hfg Tw) | 2454.1 | kJ/kg
Cpa in VF | 1077.9016 | J/kg K
Qout
Qout = Qs,out + Ql,out
Qout;tot = ma * (h2-h1) | -0.10342 | kJ/s
Qs = Cp * ma *dT = Qtot - Ql | -0.076208 | kJ/s
Ql = ma * (w2-w1) * hw | -0.027211 | kJ/s
hwe latent heat evaporization water (hfg Tw) | 2454.1 | kJ/kg |  | at T water
T dewpoint | 20.563 | C
Twater = (T DPT + T2) /2 | 20.037 | C
m water removed from system
mw = ma * (w1-w2) | 1.1088e-05 | kg/s
mw =Ql VF/hw | 1.1088e-05 | kg/s | for verification
Qin
Qin;tot = ma * (h3-h2) | 0.05199 | kJ/s
Qs = Qtot - Ql | 0.05199 | kJ/s
Ql = Qlatent = ma * (w3-w2) * hv | 0 | kJ/s | w2=w3
Energy balance
Eheat VF = Qout + Qin | -0.051429 | kJ/s | for verification
Esensible VF = Es out + Es in | -0.024218 | kJ/s
Elatent VF = El;out + El in | -0.027211 | kJ/s
Qtot VF | -0.051429 | kJ/s
| Qs | Ql | Qtot
| J s-1 m-2 | J s-1 m-2 | J s-1 m-2
Qvf | 24.218 | 27.2106 | 51.4286
Qout | -76.2082 | -27.2106 | -103.4188
Qin | 51.9903 | 0 | 51.9903
based on Blom et al., 2023
Dark period (8h)
PSYCHROMOMETRIC CHART PROPERTIES |  |  |  | http://www.flycarpet.net/en/psyonline
Point 1 |  |  |  | Point 2 |  |  | Point 3
Temperature T1 | 23 | C |  | Temperature T2 | 18.703 | C | Temperature T3 | 23 | C
R.H. 1 | 83% |  |  | R.H. 2 | 100% |  | R.H. 3
enthalphy h1 | 60.549 | kJ/kg |  | enthalphy h2 | 53.201 | kJ/kg | enthalphy h3 | 57.6293 | kJ/kg
humidity ratio w 1 | 0.014716 | kg/kg |  | humidity ratio w2 | 0.013567 | kg/kg | humidity ratio w3 | 0.013567 | kg/kg
Specific volume v1 | 0.859 | m3/kg |  | Specific volume v2 | 0.845 | m3/kg | Specific volume v3 | 0.857 | m3/kg
Air density P1 | 1.181 | kg/m3 |  | Air density p2 | 1.2 | kg/m3 | Air density p3 | 1.182 | kg/m3
Qvertical farm produced (3->1)
assumed mair same as during the day | 0.011234 | kg/s
Qlatent | 32.8 | W m-2 |  | Graamans et al., 2021, at t=23C
Qsensible | 0 | W m-2 |  | no heat losses assumed as closed box
Qtot = Qs + Ql |  |  |  | latent and sensible heat as result of the LED
Qs = 0 --> Qtot = Ql | 32.8 | J/s
Qtot = ma * dh | 0.0328 | kJ/s
dh = h1-h3 | 2.9197 | kJ/kg
h3 | 57.6293 | kJ/kg
Cpair | 1005
Qout
Qout = Qs,out + Ql,out
Qout;tot = ma * (h2-h1) | -0.082546 | kJ/s
Qs = Cp * ma *dT = Qtot - Ql | -0.048513 | kJ/s
Ql = ma * (w2-w1) * hw | -0.034033 | kJ/s
Qin
Qin;tot = ma * (h3-h2) | 0.049746 | kJ/s
Qs = Cp * ma *dT | 0.048513 | kJ/s |  | due to unprecize reading enthalpy values psychrometric chart
Ql = 0 , Qs = Qtot | 0 | kJ/s |  | w2=w3
Energy balance
Eheat VF = Qout + Qin | -0.0328 | kJ/s |  | for verification
Esensible VF = Es out + Es in | 0 | kJ/s
Elatent VF = El;out + El in | -0.034033 | kJ/s |  | due to unprecize reading enthalpy values psychrometric chart
Qtot VF | -0.034033 | kJ/s
| Qs | Ql | Qtot
| J s-1 m-2 | J s-1 m-2 | J s-1 m-2
Qvf | 0 | 32.8 | 32.8
Qout | -48.5132 | -34.0331 | -82.5463
Qin | 48.5132 | 0 | 48.5132

## VF_Cen
Vertical farm in centralised configuration
Winter | [6 empty] | Summer
Photoperiod | [6 empty] | Photoperiod
air/water HE1 (cooling and dehumidification) | [6 empty] | air/water HE1 (cooling and dehumidification)
TOTAL (All HE1) | [6 empty] | TOTAL (All HE1)
Qtot air-side = (h2-h1) * mair | -0.10342 | kJ/s | equal to Qout |  |  |  | Qtot air-side = (h2-h1) * mair | -0.10342 | kJ/s | equal to Qout
Qs air-side | -0.076208 | kJ/s | equal to Qout;s |  |  |  | Qs air-side | -0.076208 | kJ/s | equal to Qout;s
Ql air-side | -0.027211 | kJ/s | equal to Qout;l |  |  |  | Ql air-side | -0.027211 | kJ/s | equal to Qout;l
ma | 0.011234 | kg/s |  |  |  |  | ma | 0.011234 | kg/s
Qt air-side = Qt water-side = Qs water-side | -0.10342 | kJ/s | assumed no heat losses in HE |  |  |  | Qt air-side = Qt water-side = Qs water-side | -0.10342 | kJ/s | assumed no heat losses in HE
Qs = mw * Cpw * dT | [6 empty] | Qs = mw * Cpw * dT
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
mw | -0.0045774 | kg/s |  |  |  |  | mw | -0.0045774 | kg/s
water/air HE | [6 empty] | water/air HE
ε - Effectiveness HE (%) | ε = dT min fluid / dT max HE | [5 empty] | ε - Effectiveness HE (%) | ε = dT min fluid / dT max HE
ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 70% | assumption made for w/a HE counterflow |  |  |  |  | ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 70% | assumption made for w/a HE counterflow
| 70% | [6 empty] | 70%
Tc,i = Tw,i | 16.73 | C | see formulae below |  |  |  | Tc,i = Tw,i | 16.73 | C | see formulae below
Tc,o = Tw,o | 22.13 | C | see evaporator |  |  |  | Tc,o = Tw,o | 22.13 | C | see evaporator
Th,i= Ta,i | 26 | C |  |  |  |  | Th,i= Ta,i | 26 | C
Th,o = Ta,o | 19.511 | C |  |  |  |  | Th,o = Ta,o | 19.511 | C
the formulae above agrees with the formulae below from Mansour & Fath 2016 (http://dx.doi.org/10.1016/j.desal.2016.05.025) | [6 empty] | the formulae above agrees with the formulae below from Mansour & Fath 2016 (http://dx.doi.org/10.1016/j.desal.2016.05.025)
| in which | [6 empty] | in which
| Tao = Tair,out | [6 empty] | Tao = Tair,out
| Tai = Tair, in | [6 empty] | Tai = Tair, in
| Twin = Twater, in | [6 empty] | Twin = Twater, in
air/water HE2 (heating) | [6 empty] | air/water HE2 (heating)
Qhe = ma * (h3-h2) | 0.05199 | kJ/s | equal to Qin |  |  |  | Qhe = ma * (h3-h2) | 0.05199 | kJ/s | equal to Qin
Qs = mw * Cpw * dT | [6 empty] | Qs = mw * Cpw * dT
mw | 0.0027681 | kg/s |  |  |  |  | mw | 0.0027681 | kg/s
ε = Qactual / Qmax | 70% | [5 empty] | ε = Qactual / Qmax | 70%
ε = (Th,o - Th,I) / (Th,i - Tc,i) | [6 empty] | ε = (Th,o - Th,I) / (Th,i - Tc,i)
Tc,i | 19.511 | C |  |  |  |  | Tc,i | 19.511 | C
Tc,o | 24 | C |  |  |  |  | Tc,o | 24 | C
Th,i | 25.9239 | C |  |  |  |  | Th,i | 25.9239 | C
Th,o | 21.4349 | C |  |  |  |  | Th,o | 21.4349 | C
Qs air-side =- Qs water-side | 0.05199 | kJ/s | as no heat losses assumed |  |  |  | Qs air-side =- Qs water-side | 0.05199 | kJ/s | as no heat losses assumed
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
HE3 and valve 3 | [6 empty] | HE3 and valve 3
HE3 | [6 empty] | HE3
Qhe3= mw4b * Cw * dT | [6 empty] | Qhe3= mw4b * Cw * dT
Qhe3 = Qcon - Qhe2 | 0.055827 | kJ/s | 326.0325 | kWh m-2 y-1 | 55.8275 | W m-2 | Qhe3 = Qcon - Qhe2 | 0.061443 | kJ/s | 358.827 | kWh m-2 y-1 | 61.443 | W m-2
water/water HE | [6 empty] | water/water HE
ε - Effectiveness HE (%) | 80% | [5 empty] | ε - Effectiveness HE (%) | 80%
Tc,i (connection LT DHN cold) | 2.75 | C |  |  |  |  | Tc,i (connection LT DHN cold) | 11.25 | C
Tc,o (connection LT DHN hot) | 19.75 | C |  |  |  |  | Tc,o (connection LT DHN hot) | 28.25 | C
Th,i | 24 | C |  |  |  |  | Th,i | 32.5 | C
Th,o | 7 | C |  |  |  |  | Th,o | 15.5 | C
Qs air-side =- Qs water-side | 55.8275 | J/s | as no heat losses |  |  |  | Qs air-side =- Qs water-side | 61.443 | J/s | as no heat losses
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
mw2c | -0.00078489 | kg/s |  |  |  |  | mw2c | -0.00086384 | kg/s
ma 2 | 0.0032676 | kg/s |  |  |  |  | ma 2 | 0.0035963 | kg/s
valve 3 | [6 empty] | valve 3
ml = (Th - Tf) / (Th - Tl) * mf | [6 empty] | ml = (Th - Tf) / (Th - Tl) * mf
ml = mass flow low temperature in | 0.00078489 | kg/s |  |  |  |  | ml = mass flow low temperature in | 0.00086384 | kg/s
tl = low temperature in | 7 | C |  |  |  |  | tl = low temperature in | 15.5 | C
th | 24 | C |  |  |  |  | th | 32.5 | C
mf | 0.0027681 | kg/s |  |  |  |  | mf | 0.0027681 | kg/s
tf | 25.9239 | C |  |  |  |  | tf | 25.9239 | C
mh = mf - ml | 0.0019832 | kg/s |  |  |  |  | mh = mf - ml | 0.0019043 | kg/s
water-water heat pump HP1 | [6 empty] | water-water heat pump HP1
Condenser | [6 empty] | Condenser
ε = 1 - EXP (-NTU) | 90% | [5 empty] | ε = 1 - EXP (-NTU) | 90%
(- EXP (-NTU)) | -10% | [5 empty] | (- EXP (-NTU)) | -10%
NTU | 2.3026 | [5 empty] | NTU | 2.3026
Q = mw * Cpw * dT | 0.10782 | kJ/s |  |  |  |  | Q = mw * Cpw * dT | 0.11343 | kJ/s
ε | 90% | [5 empty] | ε | 90%
Tc,i | 21.4349 | C |  |  |  |  | Tc,i | 21.4349 | C
Tc,o | 24 | C |  |  |  |  | Tc,o | 32.5 | C
Th,i = Th,o = Tcon = T1 | 24.285 | C |  |  |  |  | Th,i = Th,o = Tcon = T1 | 33.7295
TD = Th - Tc,i | 2.8502 | [5 empty] | TD = Th - Tc,i | 12.2946
Evaporator | [6 empty] | Evaporator
Qhot = mh * Ch * dT | -0.10342 | kJ/s |  |  |  |  | Qhot = mh * Ch * dT | -0.10342 | kJ/s
Qcold | 0.10342 | kJ/s |  |  |  |  | Qcold | 0.10342 | kJ/s
e = (Th,i - Th,o) / (Th,i - Tc) | 90% | [5 empty] | e = (Th,i - Th,o) / (Th,i - Tc) | 90%
Th,i = Thot in | 22.13 | C |  |  |  |  | Th,i = Thot in | 22.13 | C
Th,o = Thot, out | 16.73 | C |  |  |  |  | Th,o = Thot, out | 16.73 | C
Tc,i = Tc, o = T3 | 16.13 | C |  |  |  |  | Tc,i = Tc, o = T3 | 16.13 | C
TD = Th,i - Tc | 6 | C |  |  |  |  | TD = Th,i - Tc | 6 | C
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K) |  |  | Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 24.285 | 6.5233 | 233.62 |  |  |  | 1 - Saturated liquid (100%): subcooling | 33.7295 | 8.5707 | 247.25
2 - liquid + vapour | 16.13 | 5.0631 | 233.62 |  |  |  | 2 - liquid + vapour | 16.13 | 5.0631 | 247.25
3 - Saturated vapour (100%): superheat | 16.13 | 5.0631 | 407.86 | 1.7204 |  |  | 3 - Saturated vapour (100%): superheat | 16.13 | 5.0631 | 407.86 | 1.7204
4 -liquid + vapour: highly superheated | 25.0479 | 6.5233 | 413.0479 | 1.7204 |  |  | 4 -liquid + vapour: highly superheated | 35.4829 | 8.5707 | 418.7467 | 1.7204
[7 empty] | 4 calculated with P-bar 850 | 35.1647 |  | 418.5746
[7 empty] | 4 calculated with P-base 900 | 37.4154 |  | 419.7919
[7 empty] | percentage | 0.14138
Isentropic efficiency | [6 empty] | Isentropic efficiency
E | 0.7 | [5 empty] | E | 0.7
E = (h4 - h3) / (h4' - h3) | [6 empty] | E = (h4 - h3) / (h4' - h3)
h4' | 415.2713 | kJ/kg |  |  |  |  | h4' | 423.4124 | kJ/kg
Qcold = Qev | [6 empty] | Qcold = Qev
Qcold = m * (h3-h2) | -0.10342 | kJ/s | sensible and latent heat |  |  |  | Qcold = m * (h3-h2) | -0.10342 | kJ/s | sensible and latent heat
ṁr = flow rate refrigerant | -0.00059354 | kg/s |  |  |  |  | ṁr = flow rate refrigerant | -0.00064391 | kg/s
ṁ water through evaporator | 0.0045774 | kg/s |  |  |  |  | ṁ water through evaporator | 0.0045774 | kg/s
Qhot = Qcon | [6 empty] | Qhot = Qcon
Q = mw * Cpw * dT | 107.8178 | J/s |  |  |  |  | Q = mw * Cpw * dT | 113.4332 | J/s
mw = mf | 0.010046 | kg/s |  |  |  |  | mw = mf | 0.0024501 | kg/s
Qhot = mr * (h1-h4') | 0.10782 | kJ/s |  |  |  |  | Qhot = mr * (h1-h4') | 0.11343 | kJ/s
ṁr = flow rate refrigerant | -0.00059354 | kg/s |  |  |  |  | ṁr = flow rate refrigerant | -0.00064391 | kg/s
COP cooling | [6 empty] | COP cooling
COPhp = (h4'-h1)/(h4'-h3) | 24.5101 | [5 empty] | COPhp = (h4'-h1)/(h4'-h3) | 11.327
Win = Qcon / COPhp | 0.0043989 | kJ/s |  |  |  |  | Win = Qcon / COPhp | 0.010014 | kJ/s
Win = m *dh | 0.0043989 | kJ/s |  |  |  |  | Win = m *dh | 0.010014 | kJ/s
COPref = (h3-h2) / (h4' - h3) | 23.5101 | [5 empty] | COPref = (h3-h2) / (h4' - h3) | 10.327
Win = Qev / COPref | 0.0043989 | kJ/s |  |  |  |  | Win = Qev / COPref | 0.010014 | kJ/s
Total energy use VF | [6 empty] | Total energy use VF
Energy use pumps | [6 empty] | Energy use pumps
Epump (kW) = (dp * Capacity) /( 36 * n )
dp pressure difference [bar] | [6 empty] | dp pressure difference [bar]
Capacity in m3/h | [6 empty] | Capacity in m3/h
n pumping system optimized | 72% |  | Kaya et al., 2021 |  |  |  | n pumping system optimized | 72% |  | Kaya et al., 2021
This includes the following efficiencies: motor, coupling (motor to pump), pump, piping and throttle or variable speed drive. | [6 empty] | This includes the following efficiencies: motor, coupling (motor to pump), pump, piping and throttle or variable speed drive.
Pressure (bar), P = 0,981 * h * SG | [6 empty] | Pressure (bar), P = 0,981 * h * SG
SG specific gravity fluid, for water | 1 | [5 empty] | SG specific gravity fluid, for water | 1
head = height difference between the fluid being moved and the discharge point (m) |  |  | 1 |  |  |  | head = height difference between the fluid being moved and the discharge point (m) |  |  | 1
| unit | Pump HE1-Ev | Pump HE2 - con | Total |  |  |  | unit | Pump HE1-Ev | Pump HE2 - con | Total
Head | m | 1 | 1 |  |  |  | Head | m | 1 | 1
dP (average pressure difference) | bar | 0.098 | 0.098 |  |  |  | dP (average pressure difference) | bar | 0.098 | 0.098
flow rate | kg/s | 0.0045774 | 0.0027681 |  |  |  | flow rate | kg/s | 0.0045774 | 0.0027681
Capacity | m3/s | 4.5911e-06 | 2.7764e-06 |  |  |  | Capacity | m3/s | 4.5911e-06 | 2.7764e-06
Capacity | m3/h | 0.016528 | 0.0099951 |  |  |  | Capacity | m3/h | 0.016528 | 0.0099951
n pump | % | 72% | 72% |  |  |  | n pump | % | 72% | 72%
Epump | W | 0.06249 | 0.03779 |  |  |  | Epump | W | 0.06249 | 0.03779
Epump | kWh m-2 d-1 | 0.00099984 | 0.00060464 | 0.0016045 |  |  | Epump | kWh m-2 d-1 | 0.00099984 | 0.00060464 | 0.0016045
velocity water pipes | m/s | 2 | 2 |  |  |  | velocity water pipes | m/s | 2 | 2
p water | 997 | kg/m3 |  |  |  |  | p water | 997 | kg/m3
h active (day) | 16 | hrs/yr |  |  |  |  | h active (day) | 16 | hrs/yr
Energy use fans | [6 empty] | Energy use fans
Calculations based on Graamans et al., 2020 | [6 empty] | Calculations based on Graamans et al., 2020
Including assumptions fan efficiency 65% and Uair,max 15 m/s | [6 empty] | Including assumptions fan efficiency 65% and Uair,max 15 m/s
E fan [W] = (Vair * dp) / n fan | [6 empty] | E fan [W] = (Vair * dp) / n fan
Vair in m3/s | [6 empty] | Vair in m3/s
dp, pressure difference in Pa | [6 empty] | dp, pressure difference in Pa
dp = ((Uair^2 * p air )/2 ) + dPfl | [6 empty] | dp = ((Uair^2 * p air )/2 ) + dPfl
delta Pfl = friction loss = 3.4 uair^2 + 4,9 uair | [6 empty] | delta Pfl = friction loss = 3.4 uair^2 + 4,9 uair
| unit | Indoor fan VF | [5 empty] | unit | Indoor fan VF
Air density | kg/m3 | 1.225 |  |  |  |  | Air density | kg/m3 | 1.225
Uair ducts (not farm) | m/s max | 8 |  |  |  |  | Uair ducts (not farm) | m/s max | 8
Friction loss | Pa | 256.8 |  |  |  |  | Friction loss | Pa | 256.8
Pressure difference | Pa | 296 |  |  |  |  | Pressure difference | Pa | 296
Vair | kg/s | 0.011234 |  |  |  |  | Vair | kg/s | 0.011234
Vair | m3/s | 0.0091705 |  |  |  |  | Vair | m3/s | 0.0091705
Vair | m3/h | 33.0138 |  |  |  |  | Vair | m3/h | 33.0138
n fan | % | 65% |  |  |  |  | n fan | % | 65%
E fan | kW | 0.0041761 |  |  |  |  | E fan | kW | 0.0041761
E fan | kWh d-1 | 0.066818 |  |  |  |  | E fan | kWh d-1 | 0.066818
velocity | m/s | 8 |  |  |  |  | velocity | m/s | 8
p air | 1.225 | kg/m3 |  |  |  |  | p air | 1.225 | kg/m3
Total energy use photoperiod (winter) | [6 empty] | Total energy use photoperiod (summer)
Etotal | J m-2 s-1 | J s-1 | kWh m-2 d-1 | kWh d-1 decentralised |  |  | Etotal | J m-2 s-1 | J s-1 | kWh m-2 d-1 | kWh d-1 decentralised
E HP | 4.3989 | 186446.0332 | 0.070383 | 2983.1365 |  |  | E HP | 10.0144 | 424455.8646 | 0.16023 | 6791.2938
Epump | 0.10028 | 4250.3427 | 0.0016045 | 68.0055 |  |  | Epump | 0.10028 | 4250.3427 | 0.0016045 | 68.0055
Efans | 4.1761 | 177002.0916 | 0.066818 | 2832.0335 |  |  | Efans | 4.1761 | 177002.0916 | 0.066818 | 2832.0335
ELED | 57.1429 | 2421973.6371 | 0.91429 | 38751.5782 |  |  | ELED | 57.1429 | 2421973.6371 | 0.91429 | 38751.5782
Etot | 65.8182 | 2789672.1047 | 1.0531 | 44634.7537 |  |  | Etot | 71.4336 | 3027681.9361 | 1.1429 | 48442.911
79.99%
Dark period | [6 empty] | Dark period
air/water HE1 (cooling and dehumidification) | [6 empty] | air/water HE1 (cooling and dehumidification)
TOTAL (All HE1) | [6 empty] | TOTAL (All HE1)
Qtot air-side = (h2-h1) * mair | -0.082546 | kJ/s | equal to Qout |  |  |  | Qtot air-side = (h2-h1) * mair | -0.082546 | kJ/s | equal to Qout
Qs air-side | -0.048513 | kJ/s | equal to Qout;s |  |  |  | Qs air-side | -0.048513 | kJ/s | equal to Qout;s
Ql air-side | -0.034033 | kJ/s | equal to Qout;l |  |  |  | Ql air-side | -0.034033 | kJ/s | equal to Qout;l
ma | 0.011234 | kg/s |  |  |  |  | ma | 0.011234 | kg/s
Qt air-side = Qt water-side = Qs water-side | -0.082546 | kJ/s | assumed no heat losses in HE |  |  |  | Qt air-side = Qt water-side = Qs water-side | -0.082546 | kJ/s | assumed no heat losses in HE
Qs = mw * Cpw * dT | [6 empty] | Qs = mw * Cpw * dT
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
mw | -0.0036535 | kg/s |  |  |  |  | mw | -0.0036535 | kg/s
water/air HE | [6 empty] | water/air HE
ε - Effectiveness HE (%) | ε = dT min fluid / dT max HE | [5 empty] | ε - Effectiveness HE (%) | ε = dT min fluid / dT max HE
ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 70% | assumption made for w/a HE counterflow |  |  |  |  | ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 70% | assumption made for w/a HE counterflow
| 70% | [6 empty] | 70%
Tc,i = Tw,i | 16.8614 | C |  |  |  |  | Tc,i = Tw,i | 16.8614 | C
Tc,o = Tw,o | 22.2614 | C |  |  |  |  | Tc,o = Tw,o | 22.2614 | C
Th,i= Ta,i | 23 | C |  |  |  |  | Th,i= Ta,i | 23 | C
Th,o = Ta,o | 18.703 | C |  |  |  |  | Th,o = Ta,o | 18.703 | C
air/water HE2 (heating) | [6 empty] | air/water HE2 (heating)
Qhe = ma * (h3-h2) | 0.048513 | kJ/s | equal to Qin |  |  |  | Qhe = ma * (h3-h2) | 0.048513 | kJ/s | equal to Qin
Qs = mw * Cpw * dT | [6 empty] | Qs = mw * Cpw * dT
mw | 0.0026984 | kg/s |  |  |  |  | mw | 0.0026984 | kg/s
ε = Qactual / Qmax | 70% | [5 empty] | ε = Qactual / Qmax | 70%
Tc,i | 18.703 | C |  |  |  |  | Tc,i | 18.703 | C
Tc,o | 23 | C |  |  |  |  | Tc,o | 23 | C
Th,i | 24.8416 | C |  |  |  |  | Th,i | 24.8416 | C
Th,o | 20.5446 | C |  |  |  |  | Th,o | 20.5446 | C
Qs air-side =- Qs water-side | 0.048513 | kJ/s | as no heat losses assumed |  |  |  | Qs air-side =- Qs water-side | 0.048513 | kJ/s | as no heat losses assumed
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
HE3 and valve 3 | [6 empty] | HE3 and valve 3
HE3 | [6 empty] | HE3
Qhe3= mw4b * Cw * dT | [6 empty] | Qhe3= mw4b * Cw * dT
Qhe3 = Qcon - Qhe2 | 0.037447 | kJ/s | 109.3458 | kWh m-2 y-1 | 37.4472 | W m-2 | Qhe3 = Qcon - Qhe2 | 0.041966 | kJ/s | 122.5403 | kWh m-2 y-1 | 41.9659 | W m-2
water/water HE | [6 empty] | water/water HE
ε - Effectiveness HE (%) | 80% | [5 empty] | ε - Effectiveness HE (%) | 80%
Tc,i (connection LT DHN cold) | 2.75 | C |  |  |  |  | Tc,i (connection LT DHN cold) | 11.25 | C
Tc,o (connection LT DHN hot) | 19.75 | C |  |  |  |  | Tc,o (connection LT DHN hot) | 28.25 | C
Th,i | 24 | C |  |  |  |  | Th,i | 32.5 | C
Th,o | 7 | C |  |  |  |  | Th,o | 15.5 | C
Qs air-side =- Qs water-side | 37.4472 | J/s | as no heat losses |  |  |  | Qs air-side =- Qs water-side | 41.9659 | J/s | as no heat losses
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
mw2c | -0.00052648 | kg/s |  |  |  |  | mw2c | -0.00059 | kg/s
ma 2 | 0.0021918 | kg/s |  |  |  |  | ma 2 | 0.0024563 | kg/s
valve 3 | [6 empty] | valve 3
ml = (Th - Tf) / (Th - Tl) * mf | [6 empty] | ml = (Th - Tf) / (Th - Tl) * mf
ml = mass flow low temperature in | 0.00052648 | kg/s |  |  |  |  | ml = mass flow low temperature in | 0.00059 | kg/s
tl = low temperature in | 7 | C |  |  |  |  | tl = low temperature in | 15.5 | C
th | 24 | C |  |  |  |  | th | 32.5 | C
mf | 0.0026984 | kg/s |  |  |  |  | mf | 0.0026984 | kg/s
tf | 24.8416 | C |  |  |  |  | tf | 24.8416 | C
mh = mf - ml | 0.0021719 | kg/s |  |  |  |  | mh = mf - ml | 0.0021084 | kg/s
water-water heat pump HP1 | [6 empty] | water-water heat pump HP1
Condenser | [6 empty] | Condenser
ε = 1 - EXP (-NTU) | 90% | [5 empty] | ε = 1 - EXP (-NTU) | 90%
(- EXP (-NTU)) | -10% | [5 empty] | (- EXP (-NTU)) | -10%
NTU | 2.3026 | [5 empty] | NTU | 2.3026
Q = mw * Cpw * dT | 0.08596 | kJ/s |  |  |  |  | Q = mw * Cpw * dT | 0.090479 | kJ/s
ε | 90% | [5 empty] | ε | 90%
Tc,i | 20.5446 | C |  |  |  |  | Tc,i | 20.5446 | C
Tc,o | 24 | C |  |  |  |  | Tc,o | 32.5 | C
Th,i = Th,o = Tcon = T1 | 24.3839 | C |  |  |  |  | Th,i = Th,o = Tcon = T1 | 33.8284 | C
Evaporator | [6 empty] | Evaporator
Qhot = mh * Ch * dT | -0.082546 | kJ/s |  |  |  |  | Qhot = mh * Ch * dT | -0.082546 | kJ/s
Qcold | 0.082546 | kJ/s |  |  |  |  | Qcold | 0.082546 | kJ/s
Simplified | [6 empty] | Simplified
E = Qa / Qmax | [6 empty] | E = Qa / Qmax
E = Cw * Cpw * (Th,o - Th,i) / Cmin * (Th,o - Tc) | [6 empty] | E = Cw * Cpw * (Th,o - Th,i) / Cmin * (Th,o - Tc)
Cmin = Cw * Cpw as Cref = infinite | [6 empty] | Cmin = Cw * Cpw as Cref = infinite
Thus, e = (Th,i - Th,o) / (Th,i - Tc) | 90% | [5 empty] | Thus, e = (Th,i - Th,o) / (Th,i - Tc) | 90%
Th,i = Thot in | 22.2614 | C |  |  |  |  | Th,i = Thot in | 22.2614 | C
Th,o = Thot, out | 16.8614 | C |  |  |  |  | Th,o = Thot, out | 16.8614 | C
Tc,i = Tc, o = T3 | 16.2614 | C |  |  |  |  | Tc,i = Tc, o = T3 | 16.2614 | C
TD = Th,i - Tc | 6 | C |  |  |  |  | TD = Th,i - Tc | 6 | C
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K) |  |  | Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 24.3839 | 6.5429 | 233.76 |  |  |  | 1 - Saturated liquid (100%): subcooling | 33.8284 | 8.5956 | 247.4
2 - liquid + vapour | 16.2614 | 5.0957 | 233.76 |  |  |  | 2 - liquid + vapour | 16.2614 | 5.0957 | 247.4
3 - Saturated vapour (100%): superheat | 16.2614 | 5.0957 | 407.98 | 1.7203 |  |  | 3 - Saturated vapour (100%): superheat | 16.2614 | 5.0957 | 407.98 | 1.7203
4 -liquid + vapour: highly superheated | 25.024 | 6.5429 | 413.024 | 1.7203 |  |  | 4 -liquid + vapour: highly superheated | 35.5714 | 8.5956 | 418.7823 | 1.7203
[7 empty] | 4 calculated with P-bar 850 | 35.1412 |  | 418.5496
[7 empty] | 4 calculated with P-base 900 | 37.3923 |  | 419.7668
[7 empty] | percentage | 0.19112
Isentropic efficiency | [6 empty] | Isentropic efficiency
E | 0.7 | [5 empty] | E | 0.7
E = (h4 - h3) / (h4' - h3) | [6 empty] | E = (h4 - h3) / (h4' - h3)
h4' | 415.1856 | kJ/kg |  |  |  |  | h4' | 423.4118 | kJ/kg
Qcold = Qev | [6 empty] | Qcold = Qev
Qcold = m * (h3-h2) | -0.082546 | kJ/s | sensible and latent heat |  |  |  | Qcold = m * (h3-h2) | -0.082546 | kJ/s | sensible and latent heat
ṁr = flow rate refrigerant | -0.00047381 | kg/s |  |  |  |  | ṁr = flow rate refrigerant | -0.00051405 | kg/s
ṁ water through evaporator | 0.0036535 | kg/s |  |  |  |  | ṁ water through evaporator | 0.0036535 | kg/s
Qhot = Qcon | [6 empty] | Qhot = Qcon
Q = mw * Cpw * dT | 85.9604 | J/s |  |  |  |  | Q = mw * Cpw * dT | 90.4791 | J/s
mw = mf | 0.0059457 | kg/s |  |  |  |  | mw = mf | 0.0018088 | kg/s
Qhot = mr * (h1-h4') | 0.08596 | kJ/s |  |  |  |  | Qhot = mr * (h1-h4') | 0.090479 | kJ/s
ṁr = flow rate refrigerant | -0.00047381 | kg/s |  |  |  |  | ṁr = flow rate refrigerant | -0.00051405 | kg/s
COP cooling | [6 empty] | COP cooling
COPhp = (h4'-h1)/(h4'-h3) | 25.1783 | [5 empty] | COPhp = (h4'-h1)/(h4'-h3) | 11.4058
Win = Qcon / COPhp | 0.0034141 | kJ/s |  |  |  |  | Win = Qcon / COPhp | 0.0079327 | kJ/s
Win = m *dh | 0.0034141 | kJ/s |  |  |  |  | Win = m *dh | 0.0079327 | kJ/s
COPref = (h3-h2) / (h4' - h3) | 24.1783 | [5 empty] | COPref = (h3-h2) / (h4' - h3) | 10.4058
Win = Qev / COPref | 0.0034141 | kJ/s |  |  |  |  | Win = Qev / COPref | 0.0079327 | kJ/s
Total energy use VF | [6 empty] | Total energy use VF
Energy use pumps | [6 empty] | Energy use pumps
| unit | Pump HE1-Ev | Pump HE2 - con | Total |  |  |  | unit | Pump HE1-Ev | Pump HE2 - con | Total
Head | m | 1 | 1 |  |  |  | Head | m | 1 | 1
dP (average pressure difference) | bar | 0.098 | 0.098 |  |  |  | dP (average pressure difference) | bar | 0.098 | 0.098
flow rate | kg/s | 0.0036535 | 0.0026984 |  |  |  | flow rate | kg/s | 0.0036535 | 0.0026984
Capacity | m3/s | 3.6645e-06 | 2.7065e-06 |  |  |  | Capacity | m3/s | 3.6645e-06 | 2.7065e-06
Capacity | m3/h | 0.013192 | 0.0097434 |  |  |  | Capacity | m3/h | 0.013192 | 0.0097434
n pump | % | 72% | 72% |  |  |  | n pump | % | 72% | 72%
Epump | W | 0.049878 | 0.036838 | 0.086717 |  |  | Epump | W | 0.049878 | 0.036838 | 0.086717
Epump | kWh m-2 d-1 | 0.00039903 | 0.00029471 | 0.00069373 |  |  | Epump | kWh m-2 d-1 | 0.00039903 | 0.00029471 | 0.00069373
p water | 997 | kg/m3 |  |  |  |  | p water | 997 | kg/m3
h active | 8 | hrs/yr |  |  |  |  | h active | 8 | hrs/yr
Energy use fans | [6 empty] | Energy use fans
| unit | Indoor fan VF | [5 empty] | unit | Indoor fan VF
Air density | kg/m3 | 1.225 |  |  |  |  | Air density | kg/m3 | 1.225
Uair ducts (not farm) | m/s max | 8 |  |  |  |  | Uair ducts (not farm) | m/s max | 8
Friction loss | Pa | 256.8 |  |  |  |  | Friction loss | Pa | 256.8
Pressure difference | Pa | 296 |  |  |  |  | Pressure difference | Pa | 296
Vair | kg/s | 0.011234 |  |  |  |  | Vair | kg/s | 0.011234
Vair | m3/s | 0.0091705 |  |  |  |  | Vair | m3/s | 0.0091705
Vair | m3/h | 33.0138 |  |  |  |  | Vair | m3/h | 33.0138
n fan | % | 65% | Graamans et al., 2020 |  |  |  | n fan | % | 65% | Graamans et al., 2020
E fan | kW | 0.0041761 |  |  |  |  | E fan | kW | 0.0041761
E fan | kWh d-1 | 0.033409 |  |  |  |  | E fan | kWh d-1 | 0.033409
velocity | m/s | 8 |  |  |  |  | velocity | m/s | 8
p air | 1.225 | kg/m3 |  |  |  |  | p air | 1.225 | kg/m3
Total energy use dark period (winter) | [6 empty] | Total energy use dark period (summer)
Etotal | J m-2 s-1 | J s-1 | kWh m-2 d-1 | kWh d-1 decentralised |  |  | Etotal | J m-2 s-1 | J s-1 | kWh m-2 d-1 | kWh d-1 decentralised
E HP | 3.4141 | 144703.8827 | 0.027313 | 1157.6311 |  |  | E HP | 7.9327 | 336225.5777 | 0.063462 | 2689.8046
Epump | 0.086717 | 3675.4458 | 0.00069373 | 29.4036 |  |  | Epump | 0.086717 | 3675.4458 | 0.00069373 | 29.4036
Efans | 4.1761 | 177002.0916 | 0.033409 | 1416.0167 |  |  | Efans | 4.1761 | 177002.0916 | 0.033409 | 1416.0167
ELED | 0 | 0 | 0 | 0 |  |  | ELED | 0 | 0 | 0 | 0
Etot | 7.6769 | 325381.4201 | 0.061415 | 2603.0514 |  |  | Etot | 12.1956 | 516903.1152 | 0.097564 | 4135.2249
Total energy use winter | [6 empty] | Total energy use summer
Etotal | J m-2 s-1 | J s-1 | kWh m-2 d-1 | kWh d-1 decentralised |  |  | Etotal | J m-2 s-1 | J s-1 | kWh m-2 d-1 | kWh d-1 decentralised
E HP | 7.813 | 331149.9159 | 0.097695 | 4140.7676 |  |  | E HP | 17.9471 | 760681.4423 | 0.22369 | 9481.0985
Epump | 0.187 | 7925.7886 | 0.0022982 | 97.4091 |  |  | Epump | 0.187 | 7925.7886 | 0.0022982 | 97.4091
Efans | 8.3522 | 354004.1832 | 0.10023 | 4248.0502 |  |  | Efans | 8.3522 | 354004.1832 | 0.10023 | 4248.0502
ELED | 57.1429 | 2421973.6371 | 0.91429 | 38751.5782 |  |  | ELED | 57.1429 | 2421973.6371 | 0.91429 | 38751.5782
Etot | 73.495 | 3115053.5248 | 1.1145 | 47237.805 |  |  | Etot | 83.6292 | 3544585.0512 | 1.2405 | 52578.1359
1
2
4'
3
dH = -Ws
3'
4

## Cen_year
Centralised configuration
MT + LT DHN pipes
neighbourhood connections
Temperature DHN
LT DHN (cold pipe) | HE5, Th,o
MT DHN (warm pipe) | HE5, Th,i
energy losses MT DHN | 15% |  | Loss is expressed as a percentage of total supply. For modern district heating networks a loss of 15-20% is common.
ref: https://docs.energytransitionmodel.com/main/heat-networks/#:~:text=Transport%20and%20distribution%20losses%E2%80%8B&text=In%20the%20ETM%20this%20is,15%2D20%25%20is%20common.
Total heat demand neighbourhood
Tfl, DHW | 328.15 | K | 55C DHW
Tfl, space heat | 343.15 | K | MT Radiator 70C
Tfl return DHW | 285.15 | K | use of tapwater fresh from network (12C)
Tfl space heat return | 323.15 | K | 50C return
water/water HE3; ε | 80%
|  |  |  | Qcon HP2 |  |  | Tc,o HE5 | Tc,i HE5 | Temp MT DHN | Temp LT DHN
Monthly | Heat demands | DHW demands | Total demands | Required heat DHN incl. losses | % heat | % DHW | Tfl supply (average) | Tfl return (average) | HE5 Th,i | HE5 Th,o
| kWh | kWh | kWh | kWh |  |  | C | C | C | C
jan | 4670686.5279 | 909161.8651 | 5579848.393 | 6416825.6519 | 83.71% | 16.29% | 67.556 | 43.8084 | 73.4928 | 49.7453
feb | 4008093.4124 | 909161.8651 | 4917255.2775 | 5654843.5691 | 81.51% | 18.49% | 67.2266 | 42.9741 | 73.2897 | 49.0372
mrt | 2621144.62 | 909161.8651 | 3530306.4851 | 4059852.4578 | 74.25% | 25.75% | 66.137 | 40.2138 | 72.6178 | 46.6946
apr | 1352536.9487 | 909161.8651 | 2261698.8138 | 2600953.6359 | 59.8% | 40.2% | 63.9703 | 34.7247 | 71.2817 | 42.0361
may | 0 | 926144.9381 | 926144.9381 | 1065066.6788 | 0% | 100% | 55 | 12 | 65.75 | 22.75
june | 0 | 890189.5028 | 890189.5028 | 1023717.9283 | 0% | 100% | 55 | 12 | 65.75 | 22.75
july | 0 | 919613.0428 | 919613.0428 | 1057554.9992 | 0% | 100% | 55 | 12 | 65.75 | 22.75
aug | 0 | 919900.8622 | 919900.8622 | 1057885.9915 | 0% | 100% | 55 | 12 | 65.75 | 22.75
sept | 0 | 889960.9796 | 889960.9796 | 1023455.1265 | 0% | 100% | 55 | 12 | 65.75 | 22.75
oct | 1308164.497 | 909161.8651 | 2217326.3621 | 2549925.3164 | 59% | 41% | 63.8496 | 34.419 | 71.2073 | 41.7767
nov | 1914528.3456 | 909161.8651 | 2823690.2107 | 3247243.7422 | 67.8% | 32.2% | 65.1704 | 37.7649 | 72.0217 | 44.6163
dec | 3427213.4554 | 909161.8651 | 4336375.3205 | 4986831.6186 | 79.03% | 20.97% | 66.8551 | 42.0329 | 73.0607 | 48.2385
TOTAL YEAR | 19302367.807 | 10909942.381 | 30212310.188 | 34744156.7162 | 63.89% | 36.11% | 64.5834 | 36.2779 | 71.6597 | 43.3542
uLT + cooling DHN
ATES + HE4
water/water HE; ε | 80%
Winter
Tc,i | 2.75 | C | Temperature cooling grid winter
Tc,o | 19.75 | C | Temperature uLT grid winter
Th,i (hot source ATES) | 24 | C | Design value
Th,o (cold source ATES) | 7 | C | Design value
Summer
Tc,i (cold source ATES) | 7 | C | assume no temperature losses for simplification
Tc,o (hot source ATES) | 24 | C | assume no temperature losses for simplification
Th,i | 28.25 | C | Temperature uLT grid summer
Th,o | 11.25 | C | Temperature cooling grid summer
VF temperatures
water/water HE; ε | 80% |  | Blom et al., 2023
ε = (Tc,o - Tc,i)/(Th,i - Tc,i)
ε = (Th,i - Th,o)/(Th,i - Tc,i)
WINTER
Tc,i | 2.75 | C | Temperature cooling grid winter (see ATES)
Tc,o | 19.75 | C | Temperature uLT grid winter
Th,i | 24 | C | VF temperature heat (fixed)
Th,o | 7 | C
SUMMER
Tc,i | 11.25 | C | Temperature cooling grid winter
Tc,o | 28.25 | C | Temperature uLT grid winter (see ATES)
Th,i | 32.5 | C
Th,o | 15.5 | C
uLT + cooling grid temperatures
Winter
uLT | 19.75 | C
cooling | 2.75 | C
Summer
uLT | 28.25 | C
cooling | 11.25 | C
uLT + cooling grid temperatures (HP3 +HE6a-...)
Cooling demands from dataset 'A. Energy pattern neighbourhood'
Product cooling supply temp | 268.15 | K
Floor cooling supply temp | 285.15 | K
Return product cooling | 273.15 | K
Return floor cooling | 295.15 | K
HP3 - active cooling of supermarket product cooling
Efficiency condenser/evaporator | 90%
[6 empty] | Tf supply average | Tfl return average
Monthly | Cooling demands total | Qev HP3 (Superm.) | Qev HP3 (Superm.) | product cooling | space cooling | Th,o ev | Th,i ev | T3 = Tev | Tc,o condenser | Tc,i condenser | T1 = Tcon | Qcon HP3 | Qcon HP3 | COPh | Win | Win | Qev HP3 (Superm.)
| kWh | kWh | kJ/s | % | % | C | C | C | C | C | C | kWh | kJ/s | - | kWh | kJ/s | kg/s
jan | 147608.0666 | 147608.0666 | 198.3979 | 100% | 0% | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 173317.0864 | 232.9531 | 6.7415 | 25709.0198 | 34.5551 | 2.4367
feb | 147608.0666 | 147608.0666 | 198.3979 | 100% | 0% | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 173317.0864 | 257.9123 | 6.7415 | 25709.0198 | 38.2575 | 2.4367
mrt | 147608.0666 | 147608.0666 | 198.3979 | 100% | 0% | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 173317.0864 | 232.9531 | 6.7415 | 25709.0198 | 34.5551 | 2.4367
apr | 150619.8609 | 147608.0666 | 198.3979 | 98% | 2% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 173317.0864 | 240.7182 | 6.7415 | 25709.0198 | 35.707 | 2.4367
may | 286552.176 | 147608.0666 | 198.3979 | 51.51% | 48.49% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 173317.0864 | 232.9531 | 6.7415 | 25709.0198 | 34.5551 | 2.4367
june | 592952.0472 | 147608.0666 | 198.3979 | 24.89% | 75.11% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 173317.0864 | 240.7182 | 6.7415 | 25709.0198 | 35.707 | 2.4367
july | 1012796.1697 | 147608.0666 | 198.3979 | 14.57% | 85.43% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 173317.0864 | 232.9531 | 6.7415 | 25709.0198 | 34.5551 | 2.4367
aug | 872647.3426 | 147608.0666 | 198.3979 | 16.91% | 83.09% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 173317.0864 | 232.9531 | 6.7415 | 25709.0198 | 34.5551 | 2.4367
sept | 275308.144 | 147608.0666 | 198.3979 | 53.62% | 46.38% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 173317.0864 | 240.7182 | 6.7415 | 25709.0198 | 35.707 | 2.4367
oct | 154234.014 | 147608.0666 | 198.3979 | 95.7% | 4.296% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 173317.0864 | 232.9531 | 6.7415 | 25709.0198 | 34.5551 | 2.4367
nov | 147608.0666 | 147608.0666 | 198.3979 | 100% | 0% | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 173317.0864 | 240.7182 | 6.7415 | 25709.0198 | 35.707 | 2.4367
dec | 147608.0666 | 147608.0666 | 198.3979 | 100% | 0% | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 173317.0864 | 232.9531 | 6.7415 | 25709.0198 | 34.5551 | 2.4367
TOTAL YEAR | 4083150.0871 | 1771296.7989 |  | 50% | 50% | 3.5 | 11 | 2.6667 |  |  |  | 2079805.0365 |  |  | 308508.2376
COP winter months
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 21.6389 | 6.1975 | 231.24
2 - liquid + vapour | -5.5556 | 2.3795 | 231.24
3 - Saturated vapour (100%): superheat | -5.5556 | 2.3795 | 395.54 | 1.7312
4 -liquid + vapour: highly superheated | 26.8453 | 6.1975 | 415.5714 | 1.7312
4 calculated with P-bar 600 | 26.765 |  | 415.965
4 calculated with P-bar 625 | 26.8667 |  | 415.4667
percentage | 0.78984
Isentropic efficiency
E | 0.7
E = (h4 - h3) / (h4' - h3)
h4' | 424.1563 | kJ/kg
COPhp = (h4'-h1)/(h4'-h3) | 6.7415
HE6a-.. passive cooling (floor cooling)
[6 empty] | Treturn floor cooling | Tsupply floor cooling | T DHN cold | T DHN uLT
Monthly | Cooling demands total | Q HE6a-.. | Q HE6a-.. | product cooling | space cooling | Th,i | Th,o | Tc,i | Tc,o
| kWh | kWh | kJ/s | % | % | C | C | C | C
jan | 147608.0666 | 0 | 0 | 100% | 0%
feb | 147608.0666 | 0 | 0 | 100% | 0%
mrt | 147608.0666 | 0 | 0 | 100% | 0%
apr | 150619.8609 | 3011.7943 | 4.0481 | 98% | 2% | 32.5 | 15.5 | 11.25 | 28.25
may | 286552.176 | 138944.1094 | 186.7528 | 51.51% | 48.49% | 32.5 | 15.5 | 11.25 | 28.25
june | 592952.0472 | 445343.9807 | 598.5806 | 24.89% | 75.11% | 32.5 | 15.5 | 11.25 | 28.25
july | 1012796.1697 | 865188.1031 | 1162.8872 | 14.57% | 85.43% | 32.5 | 15.5 | 11.25 | 28.25
aug | 872647.3426 | 725039.276 | 974.5152 | 16.91% | 83.09% | 32.5 | 15.5 | 11.25 | 28.25
sept | 275308.144 | 127700.0774 | 171.6399 | 53.62% | 46.38% | 32.5 | 15.5 | 11.25 | 28.25
oct | 154234.014 | 6625.9474 | 8.9058 | 95.7% | 4.296% | 32.5 | 15.5 | 11.25 | 28.25
nov | 147608.0666 | 0 | 0 | 100% | 0%
dec | 147608.0666 | 0 | 0 | 100% | 0%
TOTAL YEAR | 4083150.0871 | 2311853.2882 |  | 50% | 50%
Centralised HP (HP2)
ε - Effectiveness HE (%)
ε = dT min fluid / dT max HE
εcondenser = (Tc,o - Tc,i)/(Th,i - Tc,i) | 90%
εevaporator = (Th,i - Th,o) / (Th,i - Tcold) | 90%
Heat incl. losses DHN
Monthly | Qhot = Qcon | Qhot = Qcon | Tc,i (condenser) | Tc,o (condenser) | T1 = Tcon | Qcold = Qev | Qcold = Qev | Th,i (evaporator) | Th,o (evaporator) | T3 = Tev | COP | Win | Win
| kWh | kJ/s | C | C | C | kWh | kJ/s | C | C | C |  | kWh | kJ/s
jan | 6416825.6519 | 8624.7657 | 49.7453 | 73.4928 | 76.1315 | 3703374.1711 | 4977.6535 | 19.75 | 2.75 | 0.86111 | 2.3648 | 2713451.4808 | 3647.1122
feb | 5654843.5691 | 8414.9458 | 49.0372 | 73.2897 | 75.9845 | 3263607.7013 | 4856.5591 | 19.75 | 2.75 | 0.86111 | 2.3648 | 2391235.8678 | 3558.3867
mrt | 4059852.4578 | 5456.7909 | 46.6946 | 72.6178 | 75.4982 | 2343082.6309 | 3149.3046 | 19.75 | 2.75 | 0.86111 | 2.3648 | 1716769.8269 | 2307.4863
apr | 2600953.6359 | 3612.4356 | 42.0361 | 71.2817 | 74.5312 | 1666744.4203 | 2314.9228 | 28.25 | 11.25 | 9.3611 | 2.7841 | 934209.2156 | 1297.5128
may | 1065066.6788 | 1431.5412 | 22.75 | 65.75 | 70.5278 | 712246.6945 | 957.3208 | 28.25 | 11.25 | 9.3611 | 3.0187 | 352819.9843 | 474.2204
june | 1023717.9283 | 1421.8305 | 22.75 | 65.75 | 70.5278 | 684595.3639 | 950.8269 | 28.25 | 11.25 | 9.3611 | 3.0187 | 339122.5644 | 471.0036
july | 1057554.9992 | 1421.4449 | 22.75 | 65.75 | 70.5278 | 707223.3762 | 950.5691 | 28.25 | 11.25 | 9.3611 | 3.0187 | 350331.623 | 470.8758
aug | 1057885.9915 | 1421.8898 | 22.75 | 65.75 | 70.5278 | 707444.7221 | 950.8666 | 28.25 | 11.25 | 9.3611 | 3.0187 | 350441.2694 | 471.0232
sept | 1023455.1265 | 1421.4655 | 22.75 | 65.75 | 70.5278 | 684419.6193 | 950.5828 | 28.25 | 11.25 | 9.3611 | 3.0187 | 339035.5072 | 470.8826
oct | 2549925.3164 | 3427.319 | 41.7767 | 71.2073 | 74.4773 | 1634044.4269 | 2196.2963 | 28.25 | 11.25 | 9.3611 | 2.7841 | 915880.8895 | 1231.0227
nov | 3247243.7422 | 4510.0608 | 44.6163 | 72.0217 | 75.0668 | 1874097.7634 | 2602.9136 | 19.75 | 2.75 | 0.86111 | 2.3648 | 1373145.9789 | 1907.1472
dec | 4986831.6186 | 6702.7307 | 48.2385 | 73.0607 | 75.8187 | 2878074.6764 | 3868.3799 | 19.75 | 2.75 | 0.86111 | 2.3648 | 2108756.9422 | 2834.3507
TOTAL YEAR | 34744156.7162 |  |  |  |  | 20858955.5661 | 28726.1959 |  |  |  |  | 13885201.1501 | 19141.0243
COP Winter | [5 empty] | April + Oct | [5 empty] | May-Sept
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K) |  | Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K) |  | Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 76.1315 | 24.2153 | 315.68 |  |  | 1 - Saturated liquid (100%): subcooling | 74.5312 | 23.3877 | 312.75 |  |  | 1 - Saturated liquid (100%): subcooling | 70.5278 | 21.4121 | 305.65
2 - liquid + vapour | 0.86111 | 3.0262 | 315.68 |  |  | 2 - liquid + vapour | 9.3611 | 4.0671 | 312.75 |  |  | 2 - liquid + vapour | 9.3611 | 4.0671 | 305.65
3 - Saturated vapour (100%): superheat | 0.86111 | 3.0262 | 399.34 | 1.7273 |  | 3 - Saturated vapour (100%): superheat | 9.3611 | 4.0671 | 404.2 | 1.7231 |  | 3 - Saturated vapour (100%): superheat | 9.3611 | 4.0671 | 404.2 | 1.7231
4 -liquid + vapour: highly superheated | 83.9994 | 24.2153 | 442.2482 | 1.7273 |  | 4 -liquid + vapour: highly superheated | 81.173 | 23.3877 | 440.0804 | 1.7231 |  | 4 -liquid + vapour: highly superheated | 76.6243 | 21.4121 | 438.3726 | 1.7231
4 calculated with P-bar 2400 | 83.5397 |  | 442.0804 |  |  | 4 calculated with P-bar 2200 | 78.0385 |  | 438.9362 |  |  | 4 calculated with P-bar 2000 | 73.2277 |  | 437.0188
4 calculated with P-base 2600 | 87.8096 |  | 443.6392 |  |  | 4 calculated with P-base 2400 | 82.5561 |  | 440.5852 |  |  | 4 calculated with P-base 2400 | 78.0385 |  | 438.9362
percentage | 0.10766 |  |  |  |  | percentage | 0.69385 |  |  |  |  | percentage | 0.70605
Isentropic efficiency | [5 empty] | Isentropic efficiency | [5 empty] | Isentropic efficiency
E | 0.7 |  |  |  |  | E | 0.7 |  |  |  |  | E | 0.7
E = (h4 - h3) / (h4' - h3) | [5 empty] | E = (h4 - h3) / (h4' - h3) | [5 empty] | E = (h4 - h3) / (h4' - h3)
h4' | 460.6374 | kJ/kg |  |  |  | h4' | 455.4577 | kJ/kg |  |  |  | h4' | 453.0179 | kJ/kg
Qhot = mr * (h1-h4') | 0 | kJ/s |  |  |  | Qhot = mr * (h1-h4') | 0 | kJ/s |  |  |  | Qhot = mr * (h1-h4') | 0 | kJ/s
mr | 0 | kg/s |  |  |  | mr | 0 | kg/s |  |  |  | mr | 0 | kg/s
Qcold = m * (h3-h2) | 0 | kJ/s |  |  |  | Qcold = m * (h3-h2) | 0 | kJ/s |  |  |  | Qcold = m * (h3-h2) | 0 | kJ/s
COPhp = (h4'-h1)/(h4'-h3) | 2.3648 |  |  |  |  | COPhp = (h4'-h1)/(h4'-h3) | 2.7841 |  |  |  |  | COPhp = (h4'-h1)/(h4'-h3) | 3.0187
Win | 0 | kJ/s |  |  |  | Win | 0 | kJ/s |  |  |  | Win | 0 | kJ/s
Sizing VF
Year-round balance
Qcon HP3 +Qcon E6 + Qhe3 = Qev HP2 + Qlosses uLT DHN
Qlosses | 3128843.3349 | kWh y-1
Qev HP2 | 20858955.5661 | kWh y-1
Qcon HP3 + Qhe6 (NBH cooling) | 4391658.3247 | kWh y-1
QHE3 | 19596140.5763 | kWh y-1
QHE3 per m2 cultivation total | 462.3417 | kWh m-2 y-1
m2 cultivation | 42384.5386 | m2
Winter or summer principle
If QHE3 +Qcon HP3 < Qev HP2 + losses --> according to winter; remaining extracted from ATES QHE4
If QHE3 +Qcon HP3 > Qev HP2 + losses --> according to summer; remaining heat stored in ATES QHE4
Monthly | Qheat VF (Qhe3) | Qheat VF (Qhe3) | m flow Qhe3 | Qcon HP3+Qhe6 (NBH cooling) | Qcon HP3+Qhe6 (NBH cooling) | Qlosses uLT | Qlosses uLT | Qev (HP2) | Qev (HP2) | m flow ev HP2 | QHE4 (ATES) | QHE4 (ATES)
| kWh | kJ/s | kg/s | kWh | kJ/s | kWh | kJ/s | kWh | kJ/s | kg/s | kWh | kJ/s
jan | 1567267.4053 | 2106.5422 | 29.6162 | 173317.0864 | 232.9531 | 555506.1257 | 746.648 | 3703374.1711 | 4977.6535 | 69.9816 | 2518295.8051 | 3384.8062
feb | 1415596.3661 | 2106.5422 | 29.6162 | 173317.0864 | 257.9123 | 489541.1552 | 728.4839 | 3263607.7013 | 4856.5591 | 68.2791 | 2164235.404 | 3220.5884
mrt | 1567267.4053 | 2106.5422 | 29.6162 | 173317.0864 | 232.9531 | 351462.3946 | 472.3957 | 2343082.6309 | 3149.3046 | 44.2766 | 953960.5339 | 1282.205
apr | 1676920.3181 | 2329.056 | 32.7446 | 176328.8807 | 244.7663 | 250011.663 | 347.2384 | 1666744.4203 | 2314.9228 | 32.5459 | 63506.8846 | 88.3389 |  |  |  | Qstored | -7700775.3583 | kWh
may | 1732817.662 | 2329.056 | 32.7446 | 312261.1958 | 419.7059 | 106837.0042 | 143.5981 | 712246.6945 | 957.3208 | 13.4591 | -1225995.1591 | -1647.843 |  |  |  | Qextracted | 7700775.3583 | kWh
june | 1676920.3181 | 2329.056 | 32.7446 | 618661.067 | 839.2988 | 102689.3046 | 142.624 | 684595.3639 | 950.8269 | 13.3678 | -1508296.7167 | -2074.9039
july | 1732817.662 | 2329.056 | 32.7446 | 1038505.1895 | 1395.8403 | 106083.5064 | 142.5854 | 707223.3762 | 950.5691 | 13.3642 | -1958015.9689 | -2631.7419
aug | 1732817.662 | 2329.056 | 32.7446 | 898356.3624 | 1207.4682 | 106116.7083 | 142.63 | 707444.7221 | 950.8666 | 13.3684 | -1817612.5939 | -2443.0277
sept | 1676920.3181 | 2329.056 | 32.7446 | 301017.1638 | 412.3581 | 102662.9429 | 142.5874 | 684419.6193 | 950.5828 | 13.3644 | -1190854.9197 | -1648.2438
oct | 1732817.662 | 2329.056 | 32.7446 | 179943.0338 | 241.8589 | 245106.664 | 329.4444 | 1634044.4269 | 2196.2963 | 30.8781 | -33609.6049 | -45.1742
nov | 1516710.3922 | 2106.5422 | 29.6162 | 173317.0864 | 240.7182 | 281114.6645 | 390.437 | 1874097.7634 | 2602.9136 | 36.5948 | 465184.9493 | 646.0902
dec | 1567267.4053 | 2106.5422 | 29.6162 | 173317.0864 | 232.9531 | 431711.2015 | 580.257 | 2878074.6764 | 3868.3799 | 54.3862 | 1569201.3862 | 2109.1416
TOTAL YEAR | 19596140.5763 |  |  | 4391658.3247 |  | 3128843.3349 |  | 20858955.5661 |  |  | 0
Cpw | 4184 | J/kg K
ATES
HOT SOURCE
Monthly | System summer/winter | QHE4 extracted | QHE4 extracted | QHE4 stored | QHE4 stored | Flow rate m ATES-side
| - | kWh | kJ/s | kWh | kJ/s | kg/s
jan | winter | 2518295.8051 | 3384.8062 |  |  | 47.5875
feb | winter | 2164235.404 | 3220.5884 |  |  | 45.2788
mrt | winter | 953960.5339 | 1282.205 |  |  | 18.0267
apr | winter | 63506.8846 | 88.3389 |  |  | 1.242
may | summer |  |  | 1225995.1591 | 1647.843 | 23.1673
june | summer |  |  | 1508296.7167 | 2074.9039 | 29.1714
july | summer |  |  | 1958015.9689 | 2631.7419 | 37.0001
aug | summer |  |  | 1817612.5939 | 2443.0277 | 34.3469
sept | summer |  |  | 1190854.9197 | 1648.2438 | 23.1729
oct | winter | -33609.6049 | -45.1742 |  |  | -0.63511
nov | winter | 465184.9493 | 646.0902 |  |  | 9.0835
dec | winter | 1569201.3862 | 2109.1416 |  |  | 29.6528
TOTAL ENERGY USE
Vertical farm
| kWh m-2 y-1 | kWh y-1
Energy use fans | 36.5826 | 1550538.3225
Energy use pumps | 0.83885 | 35554.3034
HP1 | 62.6222 | 2654210.9761
LEDs | 333.7143 | 14144326.0406
Total energy use VF |  | 18384629.6427 | equally divided over the year
18384.6296
Pumps
Epump (kW) = (dp * Capacity)/ 36 * n
P = 0.981 * head * SG
SG specific gravity fluid, for water | 1
p water | 997 | kg/m3
Assumptions
Efficiency | 72% | Kaya et al., 2021
Head HE3-HE4- ev HP2 | 1 | m
Head ATES | 200 | m
Pumps DHN
Pump energy DHN | 0,2 * V [m3/y] | KoWaNet (p. 84)
Q = m * Cp * dT
| LT Grid |  |  |  |  | MT grid
Month | Q | Q | m | m | Pumps LT DHN | Q | Q | m | m | Pumps LT DHN | Total pumps DHN
| kWh | MJ/y | kg / month | m3/month | kWh | kWh | MJ/y | kg / month | m3/month | kWh | kWh
jan | 4258880.2967 | 15331969.0683 | 215554620.8003 | 216203.2305 | 43240.6461 | 6416825.6519 | 23100572.3469 | 232494336.4749 | 233193.9182 | 46638.7836 | 89879.4297
feb | 3753148.8565 | 13511335.8832 | 189958045.822 | 190529.6347 | 38105.9269 | 5654843.5691 | 20357436.8487 | 200620155.0741 | 201223.8266 | 40244.7653 | 78350.6923
mrt | 2694545.0256 | 9700362.0921 | 136378951.9188 | 136789.3199 | 27357.864 | 4059852.4578 | 14615468.8482 | 134751128.3784 | 135156.5982 | 27031.3196 | 54389.1836
apr | 1916756.0834 | 6900321.9001 | 97012736.1949 | 97304.6501 | 19460.93 | 2600953.6359 | 9363433.0893 | 76521444.593 | 76751.6997 | 15350.3399 | 34811.27
may | 819083.6986 | 2948701.3151 | 41456266.3804 | 41581.0094 | 8316.2019 | 1065066.6788 | 3834240.0435 | 21311752.6543 | 21375.8803 | 4275.1761 | 12591.3779
june | 787284.6684 | 2834224.8064 | 39846822.7194 | 39966.7229 | 7993.3446 | 1023717.9283 | 3685384.5418 | 20484373.1479 | 20546.0112 | 4109.2022 | 12102.5468
july | 813306.8826 | 2927904.7773 | 41163884.5085 | 41287.7478 | 8257.5496 | 1057554.9992 | 3807197.9971 | 21161445.5794 | 21225.1209 | 4245.0242 | 12502.5737
aug | 813561.4304 | 2928821.1496 | 41176767.9333 | 41300.6699 | 8260.134 | 1057885.9915 | 3808389.5695 | 21168068.6641 | 21231.764 | 4246.3528 | 12506.4868
sept | 787082.5622 | 2833497.2238 | 39836593.5186 | 39956.4629 | 7991.2926 | 1023455.1265 | 3684438.4554 | 20479114.5413 | 20540.7368 | 4108.1474 | 12099.4399
oct | 1879151.0909 | 6764943.9272 | 95109435.4848 | 95395.6224 | 19079.1245 | 2549925.3164 | 9179731.1389 | 74548539.0521 | 74772.8576 | 14954.5715 | 34033.696
nov | 2155212.4279 | 7758764.7404 | 109081722.2526 | 109409.9521 | 21881.9904 | 3247243.7422 | 11690077.4721 | 101950328.3036 | 102257.0996 | 20451.4199 | 42333.4103
dec | 3309785.8779 | 11915229.1604 | 167518124.513 | 168022.1911 | 33604.4382 | 4986831.6186 | 17952593.8269 | 172860533.316 | 173380.6753 | 34676.1351 | 68280.5733
Total year | 23987798.901 | 86356076.0437 |  |  |  |  | 0
Total monthly
Month | VF fans, pumps | VF HP1 | VF LED | ATES pump | Pumps DHN (4x) | Central HP2 | NBH cooling (HP3+4) | User-related electricity | EV charging | Total electricity
| MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh
jan | 132.1744 | 221.1842 | 1178.6938 | 96.7693 | 89.8794 | 2713.4515 | 25.709 | 1053.7724 | 22.6975 | 5534.3316
feb | 132.1744 | 221.1842 | 1178.6938 | 92.0744 | 78.3507 | 2391.2359 | 25.709 | 912.9277 | 22.6975 | 5055.0476
mrt | 132.1744 | 221.1842 | 1178.6938 | 36.6574 | 54.3892 | 1716.7698 | 25.709 | 949.9959 | 22.6975 | 4338.2712
apr | 132.1744 | 221.1842 | 1178.6938 | 2.5255 | 34.8113 | 934.2092 | 25.709 | 850.0233 | 22.6975 | 3402.0283
may | 132.1744 | 221.1842 | 1178.6938 | 47.1107 | 12.5914 | 352.82 | 25.709 | 840.6567 | 22.6975 | 2833.6377
june | 132.1744 | 221.1842 | 1178.6938 | 59.3201 | 12.1025 | 339.1226 | 25.709 | 807.8451 | 22.6975 | 2798.8492
july | 132.1744 | 221.1842 | 1178.6938 | 75.2397 | 12.5026 | 350.3316 | 25.709 | 815.9337 | 22.6975 | 2834.4665
aug | 132.1744 | 221.1842 | 1178.6938 | 69.8445 | 12.5065 | 350.4413 | 25.709 | 830.2678 | 22.6975 | 2843.519
sept | 132.1744 | 221.1842 | 1178.6938 | 47.1222 | 12.0994 | 339.0355 | 25.709 | 814.1013 | 22.6975 | 2792.8174
oct | 132.1744 | 221.1842 | 1178.6938 | -1.2915 | 34.0337 | 915.8809 | 25.709 | 916.5946 | 22.6975 | 3445.6766
nov | 132.1744 | 221.1842 | 1178.6938 | 18.4713 | 42.3334 | 1373.146 | 25.709 | 963.9632 | 22.6975 | 3978.3729
dec | 132.1744 | 221.1842 | 1178.6938 | 60.2989 | 68.2806 | 2108.7569 | 25.709 | 1063.0444 | 22.6975 | 4880.8398
TOTAL YEAR | 1586.0926 | 2654.211 | 14144.326 | 604.1424 | 463.8807 | 13885.2012 | 308.5082 | 10819.1261 | 272.3695 | 44737.8576
User-realted electricity and electric vehicle charging from dataset 'A. Energy pattern neighbourhood'
Heat balance
Month | Heat demand | Losses grid MT | Losses grid uLT | Qlosses DHN total | VF produce (QHE3) | ATES extracted/stored | HP2 Win | NBH cooling | Total supply | total demand
| MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh
jan | 5579.8484 | 836.9773 | 555.5061 | 1392.4834 | 1567.2674 | 2518.2958 | 2713.4515 | 173.3171 | 6972.3318 | 6972.3318
feb | 4917.2553 | 737.5883 | 489.5412 | 1227.1294 | 1415.5964 | 2164.2354 | 2391.2359 | 173.3171 | 6144.3847 | 6144.3847
mrt | 3530.3065 | 529.546 | 351.4624 | 881.0084 | 1567.2674 | 953.9605 | 1716.7698 | 173.3171 | 4411.3149 | 4411.3149
apr | 2261.6988 | 339.2548 | 250.0117 | 589.2665 | 1676.9203 | 63.5069 | 934.2092 | 176.3289 | 2850.9653 | 2850.9653
may | 926.1449 | 138.9217 | 106.837 | 245.7587 | 1732.8177 | -1225.9952 | 352.82 | 312.2612 | 1171.9037 | 1171.9037
june | 890.1895 | 133.5284 | 102.6893 | 236.2177 | 1676.9203 | -1508.2967 | 339.1226 | 618.6611 | 1126.4072 | 1126.4072
july | 919.613 | 137.942 | 106.0835 | 244.0255 | 1732.8177 | -1958.016 | 350.3316 | 1038.5052 | 1163.6385 | 1163.6385
aug | 919.9009 | 137.9851 | 106.1167 | 244.1018 | 1732.8177 | -1817.6126 | 350.4413 | 898.3564 | 1164.0027 | 1164.0027
sept | 889.961 | 133.4941 | 102.6629 | 236.1571 | 1676.9203 | -1190.8549 | 339.0355 | 301.0172 | 1126.1181 | 1126.1181
oct | 2217.3264 | 332.599 | 245.1067 | 577.7056 | 1732.8177 | -33.6096 | 915.8809 | 179.943 | 2795.032 | 2795.032
nov | 2823.6902 | 423.5535 | 281.1147 | 704.6682 | 1516.7104 | 465.1849 | 1373.146 | 173.3171 | 3528.3584 | 3528.3584
dec | 4336.3753 | 650.4563 | 431.7112 | 1082.1675 | 1567.2674 | 1569.2014 | 2108.7569 | 173.3171 | 5418.5428 | 5418.5428
TOTAL YEAR | 30212.3102 | 4531.8465 | 3128.8433 | 7660.6899 | 19596.1406 | 0 | 13885.2012 | 4391.6583 | 37873.0001 | 37873.0001
Heat demand from dataset 'A. Energy pattern neighbourhood'
Cold balane
Month | VF demand (QHE3) | NBH cooling (HP3+4) | HP2 cold produced | ATES extracted/stored | Heat gains grid | Total supply | Total demand
| MWh | MWh | MWh | MWh | MWh | MWh
jan | 1567.2674 | 173.3171 | 3703.3742 | -2518.2958 | 555.5061 | 1740.5845 | 1740.5845 | 25.709
feb | 1415.5964 | 173.3171 | 3263.6077 | -2164.2354 | 489.5412 | 1588.9135 | 1588.9135
mrt | 1567.2674 | 173.3171 | 2343.0826 | -953.9605 | 351.4624 | 1740.5845 | 1740.5845
apr | 1676.9203 | 176.3289 | 1666.7444 | -63.5069 | 250.0117 | 1853.2492 | 1853.2492
may | 1732.8177 | 312.2612 | 712.2467 | 1225.9952 | 106.837 | 2045.0789 | 2045.0789
june | 1676.9203 | 618.6611 | 684.5954 | 1508.2967 | 102.6893 | 2295.5814 | 2295.5814
july | 1732.8177 | 1038.5052 | 707.2234 | 1958.016 | 106.0835 | 2771.3229 | 2771.3229
aug | 1732.8177 | 898.3564 | 707.4447 | 1817.6126 | 106.1167 | 2631.174 | 2631.174
sept | 1676.9203 | 301.0172 | 684.4196 | 1190.8549 | 102.6629 | 1977.9375 | 1977.9375
oct | 1732.8177 | 179.943 | 1634.0444 | 33.6096 | 245.1067 | 1912.7607 | 1912.7607
nov | 1516.7104 | 173.3171 | 1874.0978 | -465.1849 | 281.1147 | 1690.0275 | 1690.0275
dec | 1567.2674 | 173.3171 | 2878.0747 | -1569.2014 | 431.7112 | 1740.5845 | 1740.5845
TOTAL YEAR | 19596.1406 | 4391.6583 | 20858.9556 | 0 |  | 23987.7989 | 23987.7989
Cold demand from dataset 'A. Energy pattern neighbourhood'

## Cen_daily
Centralised configuration
WINTER PROFILES | [12 empty] | SUMMER PROFILES
neighbourhood profile with grid concious EV | [12 empty] | neighbourhood profile with grid concious EV
Data from dataset 'A. Energy pattern neighbourhood' | [12 empty] | Data from dataset 'A. Energy pattern neighbourhood'
Assume the average total heat demand in month 5-9 (Fig 1) is the DHW demand for the other months, which is uqually divided over the days of the year. | [12 empty] | Assume the average total heat demand in month 5-9 (Fig 1) is the DHW demand for the other months, which is uqually divided over the days of the year.
Daily profile DHW follows the total heat profile of the warmest day | [12 empty] | Daily profile DHW follows the total heat profile of the warmest day
Ta | 304.35 | K | Blom et al. 2023 (31,2C constant residual heat) | [9 empty] | Ta | 304.35 | K | Blom et al. 2023 (31,2C constant residual heat)
Tfl, DHW | 328.15 | K | 55C DHW | [9 empty] | Tfl, DHW | 328.15 | K | 55C DHW
Tfl, space heat | 343.15 | K | MT Radiator 70C | [9 empty] | Tfl, space heat | 343.15 | K | MT Radiator 70C
Tfl return DHW | 285.15 | K | use of tapwater fresh from network (12C) | [9 empty] | Tfl return DHW | 285.15 | K | use of tapwater fresh from network (12C)
Tfl space heat return | 323.15 | K | 50C return | [9 empty] | Tfl space heat return | 323.15 | K | 50C return
Eff cond/evap | 90% | [11 empty] | Eff cond/evap | 90%
18 january coldest weekday 2012-2022 | [12 empty] | 24 July warmest weekday 2012-2022 | [8 empty] | summer temps LT DHN
water/water HE3; ε | 80%
WINTERDAY | Heat demands | DHW demands | Total demands | Required heat DHN incl. losses | % heat | % DHW | Tf (Tc,o HE3) | Tf (Tc,i HE3) | Th,i HE3 | Th,o HE3 |  |  | Summer day | Heat demands | DHW demands | Total demands | Required heat DHN incl. losses | % heat | % DHW | Tf (Tc,o HE3) | Tf (Tc,i HE3) | Th,i HE3 | Th,o HE3
18 January | kW | kW | kW | kW |  |  | C | C | C | C |  |  | 24 July | kW | kW | kW | kW |  |  | C | C | C | C
0:00 | 4436.4779 | 558.3164 | 4994.7943 | 5744.0135 | 88.82% | 11.18% | 68.3233 | 45.7524 | 73.966 | 51.3951 |  |  | 0:00 | 0 | 558.3164 | 558.3164 | 642.0638 | 0% | 100% | 55 | 12 | 65.75 | 22.75
1:00 | 3700.7948 | 452.3828 | 4153.1777 | 4776.1543 | 89.11% | 10.89% | 68.3661 | 45.8609 | 73.9924 | 51.4872 |  |  | 1:00 | 0 | 452.3828 | 452.3828 | 520.2403 | 0% | 100% | 55 | 12 | 65.75 | 22.75
2:00 | 3653.1934 | 455.0478 | 4108.2412 | 4724.4774 | 88.92% | 11.08% | 68.3385 | 45.7909 | 73.9754 | 51.4278 |  |  | 2:00 | 0 | 455.0478 | 455.0478 | 523.305 | 0% | 100% | 55 | 12 | 65.75 | 22.75
3:00 | 3957.8182 | 463.0428 | 4420.8611 | 5083.9902 | 89.53% | 10.47% | 68.4289 | 46.0199 | 74.0312 | 51.6221 |  |  | 3:00 | 0 | 463.0428 | 463.0428 | 532.4992 | 0% | 100% | 55 | 12 | 65.75 | 22.75
4:00 | 4253.586 | 485.6953 | 4739.2813 | 5450.1735 | 89.75% | 10.25% | 68.4628 | 46.1056 | 74.052 | 51.6949 |  |  | 4:00 | 0 | 485.6953 | 485.6953 | 558.5496 | 0% | 100% | 55 | 12 | 65.75 | 22.75
5:00 | 4296.5277 | 778.8447 | 5075.3724 | 5836.6783 | 84.65% | 15.35% | 67.6982 | 44.1687 | 73.5805 | 50.0511 |  |  | 5:00 | 0 | 778.8447 | 778.8447 | 895.6714 | 0% | 100% | 55 | 12 | 65.75 | 22.75
6:00 | 5650.3317 | 1321.1711 | 6971.5028 | 8017.2282 | 81.05% | 18.95% | 67.1573 | 42.7986 | 73.247 | 48.8883 |  |  | 6:00 | 0 | 1321.1711 | 1321.1711 | 1519.3468 | 0% | 100% | 55 | 12 | 65.75 | 22.75
7:00 | 9630.278 | 1395.1247 | 11025.4028 | 12679.2132 | 87.35% | 12.65% | 68.1019 | 45.1916 | 73.8295 | 50.9192 |  |  | 7:00 | 0 | 1395.1247 | 1395.1247 | 1604.3934 | 0% | 100% | 55 | 12 | 65.75 | 22.75
8:00 | 12145.027 | 1495.7283 | 13640.7552 | 15686.8685 | 89.03% | 10.97% | 68.3552 | 45.8332 | 73.9857 | 51.4637 |  |  | 8:00 | 0 | 1495.7283 | 1495.7283 | 1720.0875 | 0% | 100% | 55 | 12 | 65.75 | 22.75
9:00 | 13164.8072 | 1539.7007 | 14704.5079 | 16910.184 | 89.53% | 10.47% | 68.4294 | 46.021 | 74.0314 | 51.6231 |  |  | 9:00 | 0 | 1539.7007 | 1539.7007 | 1770.6558 | 0% | 100% | 55 | 12 | 65.75 | 22.75
10:00 | 12404.5562 | 1337.1611 | 13741.7172 | 15802.9748 | 90.27% | 9.731% | 68.5404 | 46.3023 | 74.0999 | 51.8619 |  |  | 10:00 | 0 | 1337.1611 | 1337.1611 | 1537.7352 | 0% | 100% | 55 | 12 | 65.75 | 22.75
11:00 | 11151.3131 | 1338.4936 | 12489.8067 | 14363.2777 | 89.28% | 10.72% | 68.3925 | 45.9277 | 74.0087 | 51.5439 |  |  | 11:00 | 0 | 1338.4936 | 1338.4936 | 1539.2676 | 0% | 100% | 55 | 12 | 65.75 | 22.75
12:00 | 10825.6561 | 1374.471 | 12200.1271 | 14030.1461 | 88.73% | 11.27% | 68.3101 | 45.7189 | 73.9579 | 51.3667 |  |  | 12:00 | 0 | 1374.471 | 1374.471 | 1580.6417 | 0% | 100% | 55 | 12 | 65.75 | 22.75
13:00 | 10651.54 | 1201.2463 | 11852.7863 | 13630.7043 | 89.87% | 10.13% | 68.4798 | 46.1488 | 74.0625 | 51.7316 |  |  | 13:00 | 0 | 1201.2463 | 1201.2463 | 1381.4333 | 0% | 100% | 55 | 12 | 65.75 | 22.75
14:00 | 10946.3057 | 1050.0079 | 11996.3136 | 13795.7607 | 91.25% | 8.753% | 68.6871 | 46.674 | 74.1904 | 52.1772 |  |  | 14:00 | 0 | 1050.0079 | 1050.0079 | 1207.5091 | 0% | 100% | 55 | 12 | 65.75 | 22.75
15:00 | 11212.4321 | 1157.2739 | 12369.706 | 14225.1619 | 90.64% | 9.356% | 68.5966 | 46.4448 | 74.1346 | 51.9828 |  |  | 15:00 | 0 | 1157.2739 | 1157.2739 | 1330.865 | 0% | 100% | 55 | 12 | 65.75 | 22.75
16:00 | 11198.3129 | 1557.0231 | 12755.3361 | 14668.6365 | 87.79% | 12.21% | 68.169 | 45.3614 | 73.8709 | 51.0633 |  |  | 16:00 | 0 | 1557.0231 | 1557.0231 | 1790.5766 | 0% | 100% | 55 | 12 | 65.75 | 22.75
17:00 | 12538.9332 | 2370.5128 | 14909.4459 | 17145.8628 | 84.1% | 15.9% | 67.6151 | 43.9582 | 73.5293 | 49.8724 |  |  | 17:00 | 0 | 2370.5128 | 2370.5128 | 2726.0897 | 0% | 100% | 55 | 12 | 65.75 | 22.75
18:00 | 14138.5762 | 2355.189 | 16493.7653 | 18967.8301 | 85.72% | 14.28% | 67.8581 | 44.5739 | 73.6792 | 50.3949 |  |  | 18:00 | 0 | 2355.189 | 2355.189 | 2708.4674 | 0% | 100% | 55 | 12 | 65.75 | 22.75
19:00 | 13087.513 | 1962.7686 | 15050.2816 | 17307.8238 | 86.96% | 13.04% | 68.0438 | 45.0443 | 73.7937 | 50.7941 |  |  | 19:00 | 0 | 1962.7686 | 1962.7686 | 2257.1839 | 0% | 100% | 55 | 12 | 65.75 | 22.75
20:00 | 12442.0153 | 1672.9504 | 14114.9657 | 16232.2106 | 88.15% | 11.85% | 68.2222 | 45.4961 | 73.9037 | 51.1776 |  |  | 20:00 | 0 | 1672.9504 | 1672.9504 | 1923.893 | 0% | 100% | 55 | 12 | 65.75 | 22.75
21:00 | 11316.6001 | 1399.7885 | 12716.3885 | 14623.8468 | 88.99% | 11.01% | 68.3488 | 45.8171 | 73.9818 | 51.45 |  |  | 21:00 | 0 | 1399.7885 | 1399.7885 | 1609.7567 | 0% | 100% | 55 | 12 | 65.75 | 22.75
22:00 | 9055.3774 | 1175.9289 | 10231.3063 | 11766.0022 | 88.51% | 11.49% | 68.276 | 45.6325 | 73.9369 | 51.2934 |  |  | 22:00 | 0 | 1175.9289 | 1175.9289 | 1352.3182 | 0% | 100% | 55 | 12 | 65.75 | 22.75
23:00 | 6585.8388 | 813.4896 | 7399.3284 | 8509.2277 | 89.01% | 10.99% | 68.3509 | 45.8222 | 73.983 | 51.4544 |  |  | 23:00 | 0 | 813.4896 | 813.4896 | 935.5131 | 0% | 100% | 55 | 12 | 65.75 | 22.75
TOTAL DAY | 222443.812 | 29711.3594 | 252155.1714 | 289978.4471 | 88.22% | 11.78% | 68.2326 | 45.5225 | 73.9101 | 51.2 |  |  | TOTAL DAY | 0 | 29711.3594 | 29711.3594 | 34168.0633 | 0% | 100% | 55 | 12 | 65.75 | 22.75
User-realted electricity and electric vehicle charging from dataset 'A. Energy pattern neighbourhood' | [12 empty] | User-realted electricity and electric vehicle charging from dataset 'A. Energy pattern neighbourhood'
Daily profile, winter | [12 empty] | Daily profile, winter
18 January (on average coldest winter weekday) | [12 empty] | 24 July warmest weekday
2.3 | C (2012-2022) | [11 empty] | 22.9 | C (2012-2022)
| URE | EV | Total | [10 empty] | URE | HP | EV | Total
| kW | kW | kW | [10 empty] | kW | kW | kW | kW
0:00 | 277.3137 | 443.4672 | 720.7809 | [9 empty] | 0:00 | 288.9848 | 0 | 443.4672 | 732.452
1:00 | 237.5549 | 389.7136 | 627.2685 | [9 empty] | 1:00 | 246.2969 | 0 | 389.7136 | 636.0105
2:00 | 217.0093 | 309.0832 | 526.0925 | [9 empty] | 2:00 | 219.9491 | 0 | 309.0832 | 529.0323
3:00 | 206.4166 | 255.3296 | 461.7462 | [9 empty] | 3:00 | 204.6696 | 0 | 255.3296 | 459.9992
4:00 | 200.7646 | 188.1376 | 388.9022 | [9 empty] | 4:00 | 200.8105 | 0 | 188.1376 | 388.9481
5:00 | 213.2419 | 134.384 | 347.6259 | [9 empty] | 5:00 | 208.5809 | 0 | 134.384 | 342.9649
6:00 | 253.9743 | 80.6304 | 334.6047 | [9 empty] | 6:00 | 233.9492 | 0 | 80.6304 | 314.5796
7:00 | 322.9072 | 174.6992 | 497.6064 | [9 empty] | 7:00 | 283.302 | 0 | 174.6992 | 458.0012
8:00 | 359.4094 | 295.6448 | 655.0542 | [9 empty] | 8:00 | 347.1998 | 0 | 295.6448 | 642.8446
9:00 | 376.9609 | 416.5904 | 793.5513 | [9 empty] | 9:00 | 393.9319 | 0 | 416.5904 | 810.5223
10:00 | 381.2817 | 349.3984 | 730.6801 | [9 empty] | 10:00 | 402.8935 | 0 | 349.3984 | 752.2919
11:00 | 370.5403 | 282.2064 | 652.7467 | [9 empty] | 11:00 | 407.6655 | 0 | 282.2064 | 689.8719
12:00 | 365.423 | 228.4528 | 593.8758 | [9 empty] | 12:00 | 415.1209 | 0 | 228.4528 | 643.5737
13:00 | 367.7989 | 255.3296 | 623.1285 | [9 empty] | 13:00 | 404.346 | 0 | 255.3296 | 659.6756
14:00 | 360.3372 | 241.8912 | 602.2284 | [9 empty] | 14:00 | 401.2686 | 0 | 241.8912 | 643.1598
15:00 | 359.8236 | 241.8912 | 601.7148 | [9 empty] | 15:00 | 405.8541 | 0 | 241.8912 | 647.7453
16:00 | 365.2218 | 268.768 | 633.9898 | [9 empty] | 16:00 | 450.9235 | 0 | 268.768 | 719.6915
17:00 | 406.2677 | 144.7212 | 550.9889 | [9 empty] | 17:00 | 542.3265 | 0 | 144.7212 | 687.0477
18:00 | 522.6252 | 403.152 | 925.7772 | [9 empty] | 18:00 | 542.0794 | 0 | 403.152 | 945.2314
19:00 | 530.3969 | 524.0976 | 1054.4945 | [9 empty] | 19:00 | 505.6715 | 0 | 524.0976 | 1029.7691
20:00 | 502.0107 | 483.7824 | 985.7931 | [9 empty] | 20:00 | 465.7749 | 0 | 483.7824 | 949.5573
21:00 | 461.4897 | 443.4672 | 904.9569 | [9 empty] | 21:00 | 416.2452 | 0 | 443.4672 | 859.7124
22:00 | 424.7429 | 403.152 | 827.8949 | [9 empty] | 22:00 | 384.2443 | 0 | 403.152 | 787.3963
23:00 | 379.8485 | 430.0288 | 809.8773 | [9 empty] | 23:00 | 340.0549 | 0 | 430.0288 | 770.0837
Neighbourhood cooling | [12 empty] | Neighbourhood cooling
Cooling demands from dataset 'A. Energy pattern neighbourhood' | [12 empty] | Cooling demands from dataset 'A. Energy pattern neighbourhood'
Tfl, product cooling supply temp | 268.15 | K | [10 empty] | Tfl, product cooling supply temp | 268.15 | K
Tfl, floor cooling supply temp | 285.15 | K | [10 empty] | Tfl, floor cooling supply temp | 285.15 | K
Tfl return product cooling | 273.15 | K | [10 empty] | Tfl return product cooling | 273.15 | K
Tfl return floor cooling | 295.15 | K | [10 empty] | Tfl return floor cooling | 295.15 | K
Efficiency condenser/evaporator | 90% | [11 empty] | Efficiency condenser/evaporator | 90%
18 january coldest weekday 2012-2022 | [12 empty] | 24 July warmest weekday 2012-2022
water/water HE3; ε | 80% | [11 empty] | water/water HE3; ε | 80%
HP3 - active cooling of supermarket product cooling
|  |  | Tf supply average | Tfl return average | [8 empty] | HP3 - active cooling of supermarket product cooling
WINTERDAY | Cooling demands total NBH | Product cooling | Cooling demands supermarket | Th,o ev | Th,i ev | T3 = Tev | Tc,o condenser | Tc,i condenser | T1 = Tcon | Qcon HP3 | COPh | Win | Summer day | Cooling demands NBH total | Cooling demands supermarket | Product cooling | Space cooling | Th,o ev | Th,i ev | T3 = Tev | Tc,o condenser | Tc,i condenser | T1 = Tcon | Qcon HP3 | COPh | Win
18 January | kW | % | kW | C | C | C | C | C | C | kW | - | kW | 24 July | kW | kW | % | % | C | C | C | C | C | C | kW | - | kW
0:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 0:00 | 466.113 | 466.113 | 100% | 0% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
1:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 1:00 | 466.113 | 466.113 | 100% | 0% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
2:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 2:00 | 466.113 | 466.113 | 100% | 0% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
3:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 3:00 | 466.113 | 466.113 | 100% | 0% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
4:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 4:00 | 466.113 | 466.113 | 100% | 0% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
5:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 5:00 | 466.113 | 466.113 | 100% | 0% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
6:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 6:00 | 872.9029 | 466.113 | 53.4% | 46.6% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
7:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 7:00 | 1564.4458 | 466.113 | 29.79% | 70.21% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
8:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 8:00 | 2215.3096 | 466.113 | 21.04% | 78.96% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
9:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 9:00 | 2784.8155 | 466.113 | 16.74% | 83.26% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
10:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 10:00 | 3150.9264 | 466.113 | 14.79% | 85.21% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
11:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 11:00 | 3720.4322 | 466.113 | 12.53% | 87.47% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
12:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 12:00 | 4045.8641 | 466.113 | 11.52% | 88.48% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
13:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 13:00 | 4493.333 | 466.113 | 10.37% | 89.63% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
14:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 14:00 | 4818.7649 | 466.113 | 9.673% | 90.33% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
15:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 15:00 | 4981.4809 | 466.113 | 9.357% | 90.64% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
16:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 16:00 | 4940.8019 | 466.113 | 9.434% | 90.57% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
17:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 17:00 | 4656.049 | 466.113 | 10.01% | 89.99% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
18:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 18:00 | 4534.012 | 466.113 | 10.28% | 89.72% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
19:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 19:00 | 1149.8837 | 466.113 | 40.54% | 59.46% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
20:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 20:00 | 1011.593 | 466.113 | 46.08% | 53.92% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
21:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 21:00 | 880.9851 | 466.113 | 52.91% | 47.09% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
22:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 22:00 | 857.9367 | 466.113 | 54.33% | 45.67% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
23:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 547.2963 | 6.7415 | 81.1833 | 23:00 | 819.5226 | 466.113 | 56.88% | 43.12% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 547.2963 | 6.7415 | 81.1833
HE6a-.. passive cooling (floor cooling)
HE6a-.. passive cooling (floor cooling)
HE6 - passive building cooling
not applicable in winter |  | Q HE6a-.. | Q HE6a-.. | [9 empty] | Summer day | Cooling demands NBH total | Qhe6 | Product cooling | Space cooling | Th,i | Th,o | Tc,i | Tc,o
[13 empty] | 24 July | kW | kW | % | % | C | C | C | C
[13 empty] | 0:00 | 466.113 | 0 | 100% | 0% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 1:00 | 466.113 | 0 | 100% | 0% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 2:00 | 466.113 | 0 | 100% | 0% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 3:00 | 466.113 | 0 | 100% | 0% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 4:00 | 466.113 | 0 | 100% | 0% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 5:00 | 466.113 | 0 | 100% | 0% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 6:00 | 872.9029 | 406.7899 | 53.4% | 46.6% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 7:00 | 1564.4458 | 1098.3327 | 29.79% | 70.21% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 8:00 | 2215.3096 | 1749.1966 | 21.04% | 78.96% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 9:00 | 2784.8155 | 2318.7024 | 16.74% | 83.26% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 10:00 | 3150.9264 | 2684.8133 | 14.79% | 85.21% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 11:00 | 3720.4322 | 3254.3192 | 12.53% | 87.47% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 12:00 | 4045.8641 | 3579.7511 | 11.52% | 88.48% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 13:00 | 4493.333 | 4027.22 | 10.37% | 89.63% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 14:00 | 4818.7649 | 4352.6519 | 9.673% | 90.33% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 15:00 | 4981.4809 | 4515.3679 | 9.357% | 90.64% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 16:00 | 4940.8019 | 4474.6889 | 9.434% | 90.57% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 17:00 | 4656.049 | 4189.936 | 10.01% | 89.99% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 18:00 | 4534.012 | 4067.899 | 10.28% | 89.72% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 19:00 | 1149.8837 | 683.7707 | 40.54% | 59.46% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 20:00 | 1011.593 | 545.48 | 46.08% | 53.92% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 21:00 | 880.9851 | 414.8721 | 52.91% | 47.09% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 22:00 | 857.9367 | 391.8236 | 54.33% | 45.67% | 32.5 | 15.5 | 11.25 | 28.25
[13 empty] | 23:00 | 819.5226 | 353.4096 | 56.88% | 43.12% | 32.5 | 15.5 | 11.25 | 28.25
DHN | [12 empty] | DHN
ATES | [12 empty] | ATES
Negative is stored, positive extracted ATES | [12 empty] | Negative is stored, positive extracted ATES
WINTERDAY | Qev HP2 | Qlosses uLT | Total demand | QVF | Qcon HP3 (NBH cooling) | QHE4 extracted/stored | Flow rate m ATES-side | Pump ATES |  |  |  |  | Summer day | Qev HP2 | Qlosses uLT | Total demand | QVF | NBH cooling | QHE4 extracted/stored | Flow rate m ATES-side | Pump ATES
18 January | kW |  | KW | kW | kW | kW | kg/s | kJ/s |  |  |  |  | 24 July | kW |  | KW | kW | kW | kW | kg/s | kJ/s
0:00 | 3315.0708 | 497.2606 | 3812.3314 | 2366.2223 | 547.2963 | 898.8127 | 12.6366 | 0.09594 |  |  |  |  | 0:00 | 429.3702 | 64.4055 | 493.7757 | 2604.2321 | 547.2963 | -2657.7528 | 37.3658 | 0.28369
1:00 | 2756.4854 | 413.4728 | 3169.9583 | 2366.2223 | 547.2963 | 256.4396 | 3.6053 | 0.027372 |  |  |  |  | 1:00 | 347.9026 | 52.1854 | 400.0879 | 2604.2321 | 547.2963 | -2751.4405 | 38.6829 | 0.29369
2:00 | 2726.6609 | 408.9991 | 3135.66 | 2366.2223 | 547.2963 | 222.1414 | 3.1231 | 0.023711 |  |  |  |  | 2:00 | 349.9521 | 52.4928 | 402.4449 | 2604.2321 | 547.2963 | -2749.0836 | 38.6498 | 0.29344
3:00 | 2934.1483 | 440.1222 | 3374.2705 | 2366.2223 | 547.2963 | 460.7519 | 6.4778 | 0.049181 |  |  |  |  | 3:00 | 356.1005 | 53.4151 | 409.5156 | 2604.2321 | 547.2963 | -2742.0128 | 38.5504 | 0.29268
4:00 | 3145.4854 | 471.8228 | 3617.3083 | 1587.182 | 547.2963 | 1482.8299 | 20.8473 | 0.15828 |  |  |  |  | 4:00 | 373.5213 | 56.0282 | 429.5495 | 1778.7037 | 547.2963 | -1896.4505 | 26.6625 | 0.20243
5:00 | 3368.5509 | 505.2826 | 3873.8335 | 1587.182 | 547.2963 | 1739.3552 | 24.4539 | 0.18566 |  |  |  |  | 5:00 | 598.9662 | 89.8449 | 688.8112 | 1778.7037 | 547.2963 | -1637.1888 | 23.0175 | 0.17475
6:00 | 4627.0224 | 694.0534 | 5321.0757 | 1587.182 | 547.2963 | 3186.5974 | 44.8009 | 0.34014 |  |  |  |  | 6:00 | 1016.0394 | 152.4059 | 1168.4453 | 1778.7037 | 954.0862 | -1564.3446 | 21.9934 | 0.16698
7:00 | 7317.6167 | 1097.6425 | 8415.2592 | 1587.182 | 547.2963 | 6280.7809 | 88.3025 | 0.67041 |  |  |  |  | 7:00 | 1072.913 | 160.937 | 1233.85 | 1778.7037 | 1645.629 | -2190.4828 | 30.7964 | 0.23381
8:00 | 9053.4396 | 1358.0159 | 10411.4556 | 2366.2223 | 547.2963 | 7497.937 | 105.4147 | 0.80033 |  |  |  |  | 8:00 | 1150.2816 | 172.5422 | 1322.8239 | 2604.2321 | 2296.4929 | -3577.9011 | 50.3023 | 0.38191
9:00 | 9759.4577 | 1463.9187 | 11223.3764 | 2366.2223 | 547.2963 | 8309.8578 | 116.8296 | 0.887 |  |  |  |  | 9:00 | 1184.0984 | 177.6148 | 1361.7131 | 2604.2321 | 2865.9987 | -4108.5178 | 57.7623 | 0.43854
10:00 | 9120.4486 | 1368.0673 | 10488.5159 | 2366.2223 | 547.2963 | 7574.9973 | 106.4981 | 0.80856 |  |  |  |  | 10:00 | 1028.3364 | 154.2505 | 1182.5869 | 2604.2321 | 3232.1097 | -4653.7549 | 65.4279 | 0.49674
11:00 | 8289.5491 | 1243.4324 | 9532.9815 | 2366.2223 | 547.2963 | 6619.4629 | 93.0641 | 0.70656 |  |  |  |  | 11:00 | 1029.3612 | 154.4042 | 1183.7653 | 2604.2321 | 3801.6155 | -5222.0823 | 73.4181 | 0.55741
12:00 | 8097.2873 | 1214.5931 | 9311.8804 | 2366.2223 | 547.2963 | 6398.3618 | 89.9556 | 0.68296 |  |  |  |  | 12:00 | 1057.0294 | 158.5544 | 1215.5838 | 2604.2321 | 4127.0474 | -5515.6958 | 77.5461 | 0.58875
13:00 | 7866.7555 | 1180.0133 | 9046.7688 | 2366.2223 | 547.2963 | 6133.2501 | 86.2284 | 0.65466 |  |  |  |  | 13:00 | 923.8119 | 138.5718 | 1062.3837 | 2604.2321 | 4574.5163 | -6116.3647 | 85.991 | 0.65286
14:00 | 7962.0153 | 1194.3023 | 9156.3175 | 2366.2223 | 547.2963 | 6242.7989 | 87.7685 | 0.66636 |  |  |  |  | 14:00 | 807.5028 | 121.1254 | 928.6283 | 2604.2321 | 4899.9482 | -6575.5521 | 92.4467 | 0.70188
15:00 | 8209.8377 | 1231.4757 | 9441.3134 | 2366.2223 | 547.2963 | 6527.7947 | 91.7753 | 0.69678 |  |  |  |  | 15:00 | 889.9952 | 133.4993 | 1023.4945 | 2604.2321 | 5062.6642 | -6643.4019 | 93.4007 | 0.70912
16:00 | 8465.7824 | 1269.8674 | 9735.6497 | 1587.182 | 547.2963 | 7601.1714 | 106.8661 | 0.81135 |  |  |  |  | 16:00 | 1197.4201 | 179.613 | 1377.0331 | 1778.7037 | 5021.9852 | -5423.6558 | 76.252 | 0.57892
17:00 | 9895.4762 | 1484.3214 | 11379.7976 | 1587.182 | 547.2963 | 9245.3193 | 129.9814 | 0.98685 |  |  |  |  | 17:00 | 1823.0299 | 273.4545 | 2096.4843 | 1778.7037 | 4737.2323 | -4419.4517 | 62.1338 | 0.47173
18:00 | 10946.9971 | 1642.0496 | 12589.0467 | 1587.182 | 547.2963 | 10454.5684 | 146.9825 | 1.1159 |  |  |  |  | 18:00 | 1811.2452 | 271.6868 | 2082.932 | 1778.7037 | 4615.1953 | -4310.967 | 60.6086 | 0.46015
19:00 | 9988.9495 | 1498.3424 | 11487.292 | 1587.182 | 547.2963 | 9352.8136 | 131.4927 | 0.99832 |  |  |  |  | 19:00 | 1509.4564 | 226.4185 | 1735.8749 | 1778.7037 | 1231.067 | -1273.8958 | 17.9099 | 0.13598
20:00 | 9368.1756 | 1405.2263 | 10773.4019 | 2366.2223 | 547.2963 | 7859.8833 | 110.5034 | 0.83897 |  |  |  |  | 20:00 | 1286.5734 | 192.986 | 1479.5594 | 2604.2321 | 1092.7763 | -2217.4491 | 31.1755 | 0.23669
21:00 | 8439.9327 | 1265.9899 | 9705.9226 | 2366.2223 | 547.2963 | 6792.404 | 95.4955 | 0.72502 |  |  |  |  | 21:00 | 1076.4996 | 161.4749 | 1237.9746 | 2604.2321 | 962.1684 | -2328.4259 | 32.7357 | 0.24854
22:00 | 6790.5708 | 1018.5856 | 7809.1564 | 2366.2223 | 547.2963 | 4895.6378 | 68.8286 | 0.52256 |  |  |  |  | 22:00 | 904.3417 | 135.6513 | 1039.9929 | 2604.2321 | 939.12 | -2503.3592 | 35.1951 | 0.26721
23:00 | 4910.9724 | 736.6459 | 5647.6183 | 2366.2223 | 547.2963 | 2734.0997 | 38.4391 | 0.29184 |  |  |  |  | 23:00 | 625.6097 | 93.8415 | 719.4512 | 2604.2321 | 900.7059 | -2785.4868 | 39.1616 | 0.29732
Central HP2 | [12 empty] | HP2 connecting VF to LT DHN
WINTERDAY | Qcon | Tc,o | Tc,i | T1 = Tcon | Qev | COP | Win | [5 empty] | Summer day | Qcon | Tc,o | Tc,i | T1 = Tcon | Qev | COP | Win
Qcon HP3 +Qcon E6 + Qhe3 = Qev HP2 + Qlosses uLT DHN | kW | C | C | C | kW | - | kW | [5 empty] | 24 July | kW | C | C | C | kW | - | kW
0:00 | 5744.0135 | 73.966 | 51.3951 | 76.4739 | 3315.0708 | 2.3648 | 2428.9427 | [5 empty] | 0:00 | 642.0638 | 65.75 | 22.75 | 70.5278 | 429.3702 | 3.0187 | 212.6937
1:00 | 4776.1543 | 73.9924 | 51.4872 | 76.493 | 2756.4854 | 2.3648 | 2019.6689 | [5 empty] | 1:00 | 520.2403 | 65.75 | 22.75 | 70.5278 | 347.9026 | 3.0187 | 172.3377
Qcon HP3 + Qhe6 (NBH cooling) | 4724.4774 | 73.9754 | 51.4278 | 76.4807 | 2726.6609 | 2.3648 | 1997.8165 | [5 empty] | 2:00 | 523.305 | 65.75 | 22.75 | 70.5278 | 349.9521 | 3.0187 | 173.353
3:00 | 5083.9902 | 74.0312 | 51.6221 | 76.521 | 2934.1483 | 2.3648 | 2149.8419 | [5 empty] | 3:00 | 532.4992 | 65.75 | 22.75 | 70.5278 | 356.1005 | 3.0187 | 176.3987
4:00 | 5450.1735 | 74.052 | 51.6949 | 76.5362 | 3145.4854 | 2.3648 | 2304.688 | [5 empty] | 4:00 | 558.5496 | 65.75 | 22.75 | 70.5278 | 373.5213 | 3.0187 | 185.0283
5:00 | 5836.6783 | 73.5805 | 50.0511 | 76.1949 | 3368.5509 | 2.3648 | 2468.1274 | [5 empty] | 5:00 | 895.6714 | 65.75 | 22.75 | 70.5278 | 598.9662 | 3.0187 | 296.7051
6:00 | 8017.2282 | 73.247 | 48.8883 | 75.9536 | 4627.0224 | 2.3648 | 3390.2058 | [5 empty] | 6:00 | 1519.3468 | 65.75 | 22.75 | 70.5278 | 1016.0394 | 3.0187 | 503.3074
7:00 | 12679.2132 | 73.8295 | 50.9192 | 76.3751 | 7317.6167 | 2.3648 | 5361.5965 | [5 empty] | 7:00 | 1604.3934 | 65.75 | 22.75 | 70.5278 | 1072.913 | 3.0187 | 531.4804
8:00 | 15686.8685 | 73.9857 | 51.4637 | 76.4882 | 9053.4396 | 2.3648 | 6633.4289 | [5 empty] | 8:00 | 1720.0875 | 65.75 | 22.75 | 70.5278 | 1150.2816 | 3.0187 | 569.8059
9:00 | 16910.184 | 74.0314 | 51.6231 | 76.5213 | 9759.4577 | 2.3648 | 7150.7263 | [5 empty] | 9:00 | 1770.6558 | 65.75 | 22.75 | 70.5278 | 1184.0984 | 3.0187 | 586.5574
10:00 | 15802.9748 | 74.0999 | 51.8619 | 76.5708 | 9120.4486 | 2.3648 | 6682.5262 | [5 empty] | 10:00 | 1537.7352 | 65.75 | 22.75 | 70.5278 | 1028.3364 | 3.0187 | 509.3988
11:00 | 14363.2777 | 74.0087 | 51.5439 | 76.5048 | 8289.5491 | 2.3648 | 6073.7285 | [5 empty] | 11:00 | 1539.2676 | 65.75 | 22.75 | 70.5278 | 1029.3612 | 3.0187 | 509.9065
12:00 | 14030.1461 | 73.9579 | 51.3667 | 76.468 | 8097.2873 | 2.3648 | 5932.8588 | [5 empty] | 12:00 | 1580.6417 | 65.75 | 22.75 | 70.5278 | 1057.0294 | 3.0187 | 523.6123
13:00 | 13630.7043 | 74.0625 | 51.7316 | 76.5438 | 7866.7555 | 2.3648 | 5763.9488 | [5 empty] | 13:00 | 1381.4333 | 65.75 | 22.75 | 70.5278 | 923.8119 | 3.0187 | 457.6214
14:00 | 13795.7607 | 74.1904 | 52.1772 | 76.6363 | 7962.0153 | 2.3648 | 5833.7454 | [5 empty] | 14:00 | 1207.5091 | 65.75 | 22.75 | 70.5278 | 807.5028 | 3.0187 | 400.0063
15:00 | 14225.1619 | 74.1346 | 51.9828 | 76.5959 | 8209.8377 | 2.3648 | 6015.3242 | [5 empty] | 15:00 | 1330.865 | 65.75 | 22.75 | 70.5278 | 889.9952 | 3.0187 | 440.8698
16:00 | 14668.6365 | 73.8709 | 51.0633 | 76.405 | 8465.7824 | 2.3648 | 6202.8541 | [5 empty] | 16:00 | 1790.5766 | 65.75 | 22.75 | 70.5278 | 1197.4201 | 3.0187 | 593.1565
17:00 | 17145.8628 | 73.5293 | 49.8724 | 76.1578 | 9895.4762 | 2.3648 | 7250.3866 | [5 empty] | 17:00 | 2726.0897 | 65.75 | 22.75 | 70.5278 | 1823.0299 | 3.0187 | 903.0598
18:00 | 18967.8301 | 73.6792 | 50.3949 | 76.2663 | 10946.9971 | 2.3648 | 8020.833 | [5 empty] | 18:00 | 2708.4674 | 65.75 | 22.75 | 70.5278 | 1811.2452 | 3.0187 | 897.2222
19:00 | 17307.8238 | 73.7937 | 50.7941 | 76.3492 | 9988.9495 | 2.3648 | 7318.8743 | [5 empty] | 19:00 | 2257.1839 | 65.75 | 22.75 | 70.5278 | 1509.4564 | 3.0187 | 747.7274
20:00 | 16232.2106 | 73.9037 | 51.1776 | 76.4288 | 9368.1756 | 2.3648 | 6864.035 | [5 empty] | 20:00 | 1923.893 | 65.75 | 22.75 | 70.5278 | 1286.5734 | 3.0187 | 637.3196
21:00 | 14623.8468 | 73.9818 | 51.45 | 76.4853 | 8439.9327 | 2.3648 | 6183.9141 | [5 empty] | 21:00 | 1609.7567 | 65.75 | 22.75 | 70.5278 | 1076.4996 | 3.0187 | 533.2571
22:00 | 11766.0022 | 73.9369 | 51.2934 | 76.4528 | 6790.5708 | 2.3648 | 4975.4315 | [5 empty] | 22:00 | 1352.3182 | 65.75 | 22.75 | 70.5278 | 904.3417 | 3.0187 | 447.9766
23:00 | 8509.2277 | 73.983 | 51.4544 | 76.4862 | 4910.9724 | 2.3648 | 3598.2552 | [5 empty] | 23:00 | 935.5131 | 65.75 | 22.75 | 70.5278 | 625.6097 | 3.0187 | 309.9033
Vertical farm | [12 empty] | Vertical farm
| Light (16h) | Dark (8h) | [11 empty] | Light (16h) | Dark (8h)
LED | 38751.5782 | 0 | kWh d-1 | [9 empty] | LED | 38751.5782 | 0 | kWh d-1
| 2421.9736 | 0 | kW | [10 empty] | 2421.9736 | 0 | kW
HP1 | 2983.1365 | 1157.6311 | kWh d-1 | [9 empty] | HP1 | 6791.2938 | 2689.8046 | kWh d-1
| 186.446 | 144.7039 | kW | [10 empty] | 424.4559 | 336.2256 | kW
Fans, pumps | 2900.0389 | 1445.4203 | kWh d-1 | [9 empty] | Fans, pumps | 2900.0389 | 1445.4203 | kWh d-1
| 181.2524 | 180.6775 | kW | [10 empty] | 181.2524 | 180.6775 | kW
Electricity profile | [12 empty] | Electricity profile
| VF fans, pumps | VF HP1 | VF LED | Total | [9 empty] | VF fans, pumps | VF HP1 | VF LED | Total
| kW | kW | kW | kW | [9 empty] | kW | kW | kW | kW
0:00 | 181.2524 | 186.446 | 2421.9736 | 2789.6721 | [8 empty] | 0:00 | 181.2524 | 424.4559 | 2421.9736 | 3027.6819
1:00 | 181.2524 | 186.446 | 2421.9736 | 2789.6721 | [8 empty] | 1:00 | 181.2524 | 424.4559 | 2421.9736 | 3027.6819
2:00 | 181.2524 | 186.446 | 2421.9736 | 2789.6721 | [8 empty] | 2:00 | 181.2524 | 424.4559 | 2421.9736 | 3027.6819
3:00 | 180.6775 | 186.446 | 2421.9736 | 2789.0972 | [8 empty] | 3:00 | 180.6775 | 424.4559 | 2421.9736 | 3027.107
4:00 | 180.6775 | 144.7039 | 0 | 325.3814 | [8 empty] | 4:00 | 180.6775 | 336.2256 | 0 | 516.9031
5:00 | 180.6775 | 144.7039 | 0 | 325.3814 | [8 empty] | 5:00 | 180.6775 | 336.2256 | 0 | 516.9031
6:00 | 180.6775 | 144.7039 | 0 | 325.3814 | [8 empty] | 6:00 | 180.6775 | 336.2256 | 0 | 516.9031
7:00 | 180.6775 | 144.7039 | 0 | 325.3814 | [8 empty] | 7:00 | 180.6775 | 336.2256 | 0 | 516.9031
8:00 | 180.6775 | 186.446 | 2421.9736 | 2789.0972 | [8 empty] | 8:00 | 180.6775 | 424.4559 | 2421.9736 | 3027.107
9:00 | 180.6775 | 186.446 | 2421.9736 | 2789.0972 | [8 empty] | 9:00 | 180.6775 | 424.4559 | 2421.9736 | 3027.107
10:00 | 180.6775 | 186.446 | 2421.9736 | 2789.0972 | [8 empty] | 10:00 | 180.6775 | 424.4559 | 2421.9736 | 3027.107
11:00 | 181.2524 | 186.446 | 2421.9736 | 2789.6721 | [8 empty] | 11:00 | 181.2524 | 424.4559 | 2421.9736 | 3027.6819
12:00 | 181.2524 | 186.446 | 2421.9736 | 2789.6721 | [8 empty] | 12:00 | 181.2524 | 424.4559 | 2421.9736 | 3027.6819
13:00 | 181.2524 | 186.446 | 2421.9736 | 2789.6721 | [8 empty] | 13:00 | 181.2524 | 424.4559 | 2421.9736 | 3027.6819
14:00 | 181.2524 | 186.446 | 2421.9736 | 2789.6721 | [8 empty] | 14:00 | 181.2524 | 424.4559 | 2421.9736 | 3027.6819
15:00 | 181.2524 | 186.446 | 2421.9736 | 2789.6721 | [8 empty] | 15:00 | 181.2524 | 424.4559 | 2421.9736 | 3027.6819
16:00 | 181.2524 | 144.7039 | 0 | 325.9563 | [8 empty] | 16:00 | 181.2524 | 336.2256 | 0 | 517.478
17:00 | 181.2524 | 144.7039 | 0 | 325.9563 | [8 empty] | 17:00 | 181.2524 | 336.2256 | 0 | 517.478
18:00 | 181.2524 | 144.7039 | 0 | 325.9563 | [8 empty] | 18:00 | 181.2524 | 336.2256 | 0 | 517.478
19:00 | 181.2524 | 144.7039 | 0 | 325.9563 | [8 empty] | 19:00 | 181.2524 | 336.2256 | 0 | 517.478
20:00 | 181.2524 | 186.446 | 2421.9736 | 2789.6721 | [8 empty] | 20:00 | 181.2524 | 424.4559 | 2421.9736 | 3027.6819
21:00 | 181.2524 | 186.446 | 2421.9736 | 2789.6721 | [8 empty] | 21:00 | 181.2524 | 424.4559 | 2421.9736 | 3027.6819
22:00 | 181.2524 | 186.446 | 2421.9736 | 2789.6721 | [8 empty] | 22:00 | 181.2524 | 424.4559 | 2421.9736 | 3027.6819
23:00 | 181.2524 | 186.446 | 2421.9736 | 2789.6721 | [8 empty] | 23:00 | 181.2524 | 424.4559 | 2421.9736 | 3027.6819
Pumps DHN | [12 empty] | Electricity profile
Pump energy DHN | 0,2 * V [m3/y] | KoWaNet (p. 84) |  | 122448.9796 | [8 empty] | Pump energy DHN | 0,2 * V [m3/y] | KoWaNet (p. 84) |  | 122448.9796
Q = m * Cp * dT | [12 empty] | Q = m * Cp * dT
| LT Grid |  |  |  |  | MT grid | [7 empty] | LT Grid |  |  |  |  | MT grid
Month | Q | Q | m | m | Pumps LT DHN | Q | Q | m | m | Pumps LT DHN | Total pumps DHN |  | Month | Q | Q | m | m | Pumps LT DHN | Q | Q | m | m | Pumps LT DHN | Total pumps DHN
| kW | MJ/h | kg / h | m3/h | kW | kW | MJ/h | kg / h | m3/h | kW | kW |  |  | kW | MJ/h | kg / h | m3/h | kW | kW | MJ/h | kg / h | m3/h | kW | kW
0:00 | 3812.3314 | 13724.3929 | 53598.1803 | 53.7595 | 10.7519 | 5744.0135 | 20678.4484 | 60823.9022 | 61.0069 | 12.2014 | 22.9533 |  | 0:00 | 493.7757 | 1777.5925 | 6942.0718 | 6.963 | 1.3926 | 642.0638 | 2311.4298 | 3568.7661 | 3.5795 | 0.7159 | 2.1085
1:00 | 3169.9583 | 11411.8498 | 44566.9534 | 44.7011 | 8.9402 | 4776.1543 | 17194.1555 | 50722.7238 | 50.8753 | 10.1751 | 19.1153 |  | 1:00 | 400.0879 | 1440.3166 | 5624.9007 | 5.6418 | 1.1284 | 520.2403 | 1872.865 | 2891.6374 | 2.9003 | 0.58007 | 1.7084
2:00 | 3135.66 | 11288.376 | 44084.7488 | 44.2174 | 8.8435 | 4724.4774 | 17008.1185 | 50079.7363 | 50.2304 | 10.0461 | 18.8896 |  | 2:00 | 402.4449 | 1448.8015 | 5658.037 | 5.6751 | 1.135 | 523.305 | 1883.8981 | 2908.6721 | 2.9174 | 0.58348 | 1.7185
3:00 | 3374.2705 | 12147.3739 | 47439.4126 | 47.5822 | 9.5164 | 5083.9902 | 18302.3648 | 54223.8039 | 54.387 | 10.8774 | 20.3938 |  | 3:00 | 409.5156 | 1474.2563 | 5757.4462 | 5.7748 | 1.155 | 532.4992 | 1916.9973 | 2959.7762 | 2.9687 | 0.59374 | 1.7487
4:00 | 3617.3083 | 13022.3097 | 50856.319 | 51.0093 | 10.2019 | 5450.1735 | 19620.6245 | 58264.3695 | 58.4397 | 11.6879 | 21.8898 |  | 4:00 | 429.5495 | 1546.3782 | 6039.1054 | 6.0573 | 1.2115 | 558.5496 | 2010.7785 | 3104.571 | 3.1139 | 0.62278 | 1.8342
5:00 | 3873.8335 | 13945.8006 | 54462.8486 | 54.6267 | 10.9253 | 5836.6783 | 21012.0418 | 59287.3094 | 59.4657 | 11.8931 | 22.8185 |  | 5:00 | 688.8112 | 2479.7203 | 9684.1073 | 9.7132 | 1.9426 | 895.6714 | 3224.417 | 4978.3861 | 4.9934 | 0.99867 | 2.9413
6:00 | 5321.0757 | 19155.8727 | 74809.8603 | 75.035 | 15.007 | 8017.2282 | 28862.0216 | 78664.3276 | 78.901 | 15.7802 | 30.7872 |  | 6:00 | 1168.4453 | 4206.4032 | 16427.3608 | 16.4768 | 3.2954 | 1519.3468 | 5469.6484 | 8444.9441 | 8.4704 | 1.6941 | 4.9894
7:00 | 8415.2592 | 30294.9332 | 118311.4836 | 118.6675 | 23.7335 | 12679.2132 | 45645.1674 | 132272.2538 | 132.6703 | 26.5341 | 50.2676 |  | 7:00 | 1233.85 | 4441.8599 | 17346.8954 | 17.3991 | 3.4798 | 1604.3934 | 5775.8163 | 8917.6565 | 8.9445 | 1.7889 | 5.2687
8:00 | 10411.4556 | 37481.2401 | 146376.3298 | 146.8168 | 29.3634 | 15686.8685 | 56472.7267 | 166470.7586 | 166.9717 | 33.3943 | 62.7577 |  | 8:00 | 1322.8239 | 4762.1659 | 18597.7938 | 18.6538 | 3.7308 | 1720.0875 | 6192.315 | 9560.7158 | 9.5895 | 1.9179 | 5.6486
9:00 | 11223.3764 | 40404.155 | 157791.2552 | 158.2661 | 31.6532 | 16910.184 | 60876.6625 | 180362.9872 | 180.9057 | 36.1811 | 67.8344 |  | 9:00 | 1361.7131 | 4902.1673 | 19144.544 | 19.2022 | 3.8404 | 1770.6558 | 6374.3608 | 9841.7881 | 9.8714 | 1.9743 | 5.8147
10:00 | 10488.5159 | 37758.6574 | 147459.7336 | 147.9034 | 29.5807 | 15802.9748 | 56890.7093 | 169844.0716 | 170.3551 | 34.071 | 63.6517 |  | 10:00 | 1182.5869 | 4257.3127 | 16626.1791 | 16.6762 | 3.3352 | 1537.7352 | 5535.8469 | 8547.1522 | 8.5729 | 1.7146 | 5.0498
11:00 | 9532.9815 | 34318.7334 | 134025.7213 | 134.429 | 26.8858 | 14363.2777 | 51707.7996 | 152812.3963 | 153.2722 | 30.6544 | 57.5402 |  | 11:00 | 1183.7653 | 4261.5552 | 16642.7473 | 16.6928 | 3.3386 | 1539.2676 | 5541.3634 | 8555.6695 | 8.5814 | 1.7163 | 5.0548
12:00 | 9311.8804 | 33522.7694 | 130917.2252 | 131.3112 | 26.2622 | 14030.1461 | 50508.5261 | 148433.3309 | 148.88 | 29.776 | 56.0382 |  | 12:00 | 1215.5838 | 4376.1017 | 17090.0884 | 17.1415 | 3.4283 | 1580.6417 | 5690.3099 | 8785.6377 | 8.8121 | 1.7624 | 5.1907
13:00 | 9046.7688 | 32568.3676 | 127189.9782 | 127.5727 | 25.5145 | 13630.7043 | 49070.5354 | 145887.7217 | 146.3267 | 29.2653 | 54.7799 |  | 13:00 | 1062.3837 | 3824.5814 | 14936.2237 | 14.9812 | 2.9962 | 1381.4333 | 4973.1599 | 7678.3833 | 7.7015 | 1.5403 | 4.5365
14:00 | 9156.3175 | 32962.7431 | 128730.142 | 129.1175 | 25.8235 | 13795.7607 | 49664.7384 | 149786.3047 | 150.237 | 30.0474 | 55.8709 |  | 14:00 | 928.6283 | 3343.0617 | 13055.7341 | 13.095 | 2.619 | 1207.5091 | 4347.0327 | 6711.6651 | 6.7319 | 1.3464 | 3.9654
15:00 | 9441.3134 | 33988.7281 | 132736.9443 | 133.1364 | 26.6273 | 14225.1619 | 51210.5829 | 153481.5782 | 153.9434 | 30.7887 | 57.416 |  | 15:00 | 1023.4945 | 3684.5801 | 14389.4734 | 14.4328 | 2.8866 | 1330.865 | 4791.1141 | 7397.3111 | 7.4196 | 1.4839 | 4.3705
16:00 | 9735.6497 | 35048.339 | 136875.0665 | 137.2869 | 27.4574 | 14668.6365 | 52807.0914 | 153715.9751 | 154.1785 | 30.8357 | 58.2931 |  | 16:00 | 1377.0331 | 4957.3193 | 19359.9305 | 19.4182 | 3.8836 | 1790.5766 | 6446.0758 | 9952.5135 | 9.9825 | 1.9965 | 5.8801
17:00 | 11379.7976 | 40967.2715 | 159990.4066 | 160.4718 | 32.0944 | 17145.8628 | 61725.1062 | 173224.9816 | 173.7462 | 34.7492 | 66.8436 |  | 17:00 | 2096.4843 | 7547.3436 | 29474.8108 | 29.5635 | 5.9127 | 2726.0897 | 9813.9228 | 15152.3505 | 15.1979 | 3.0396 | 8.9523
18:00 | 12589.0467 | 45320.5681 | 176991.4338 | 177.524 | 35.5048 | 18967.8301 | 68284.1883 | 194699.1525 | 195.285 | 39.057 | 74.5618 |  | 18:00 | 2082.932 | 7498.5553 | 29284.2766 | 29.3724 | 5.8745 | 2708.4674 | 9750.4826 | 15054.401 | 15.0997 | 3.0199 | 8.8944
19:00 | 11487.292 | 41354.2511 | 161501.6868 | 161.9876 | 32.3975 | 17307.8238 | 62308.1658 | 179858.9056 | 180.4001 | 36.08 | 68.4776 |  | 19:00 | 1735.8749 | 6249.1496 | 24404.9445 | 24.4784 | 4.8957 | 2257.1839 | 8125.8619 | 12546.044 | 12.5838 | 2.5168 | 7.4124
20:00 | 10773.4019 | 38784.2469 | 151464.9916 | 151.9208 | 30.3842 | 16232.2106 | 58435.9581 | 170711.3369 | 171.225 | 34.245 | 64.6292 |  | 20:00 | 1479.5594 | 5326.4137 | 20801.3631 | 20.864 | 4.1728 | 1923.893 | 6926.0147 | 10693.5222 | 10.7257 | 2.1451 | 6.3179
21:00 | 9705.9226 | 34941.3213 | 136457.1277 | 136.8677 | 27.3735 | 14623.8468 | 52645.8485 | 155122.3572 | 155.5891 | 31.1178 | 58.4914 |  | 21:00 | 1237.9746 | 4456.7085 | 17404.884 | 17.4573 | 3.4915 | 1609.7567 | 5795.1242 | 8947.4672 | 8.9744 | 1.7949 | 5.2863
22:00 | 7809.1564 | 28112.9631 | 109790.1868 | 110.1205 | 22.0241 | 11766.0022 | 42357.6081 | 124192.0712 | 124.5658 | 24.9132 | 46.9373 |  | 22:00 | 1039.9929 | 3743.9746 | 14621.4281 | 14.6654 | 2.9331 | 1352.3182 | 4868.3456 | 7516.5538 | 7.5392 | 1.5078 | 4.4409
23:00 | 5647.6183 | 20331.4259 | 79400.7747 | 79.6397 | 15.9279 | 8509.2277 | 30633.2195 | 90274.1546 | 90.5458 | 18.1092 | 34.0371 |  | 23:00 | 719.4512 | 2590.0243 | 10114.8803 | 10.1453 | 2.0291 | 935.5131 | 3367.847 | 5199.837 | 5.2155 | 1.0431 | 3.0722
Total | [12 empty] | Total
Electricity profile | [12 empty] | Electricity profile
| VF fans, pumps | VF HP1 | VF LED | Central HP2 | ATES pump | DHN pumps | NBH cooling | URE | EV charging | Total |  |  |  | VF fans, pumps | VF HP1 | VF LED | Central HP2 | ATES pump | DHN pumps | NBH cooling | URE | EV charging | Total
| kW | kW | kW | kW | kW | kW | kW | kW | kW | kW |  |  |  | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW
0:00 | 181.2524 | 186.446 | 2421.9736 | 2428.9427 | 0.09594 | 22.9533 | 81.1833 | 277.3137 | 44.3467 | 5644.5078 |  |  | 0:00 | 181.2524 | 424.4559 | 2421.9736 | 212.6937 | 0.28369 | 2.1085 | 81.1833 | 288.9848 | 44.3467 | 3657.2826
1:00 | 181.2524 | 186.446 | 2421.9736 | 2019.6689 | 0.027372 | 19.1153 | 81.1833 | 237.5549 | 38.9714 | 5186.1932 |  |  | 1:00 | 181.2524 | 424.4559 | 2421.9736 | 172.3377 | 0.29369 | 1.7084 | 81.1833 | 246.2969 | 38.9714 | 3568.4734
2:00 | 181.2524 | 186.446 | 2421.9736 | 1997.8165 | 0.023711 | 18.8896 | 81.1833 | 217.0093 | 30.9083 | 5135.5028 |  |  | 2:00 | 181.2524 | 424.4559 | 2421.9736 | 173.353 | 0.29344 | 1.7185 | 81.1833 | 219.9491 | 30.9083 | 3535.0876
3:00 | 180.6775 | 186.446 | 2421.9736 | 2149.8419 | 0.049181 | 20.3938 | 81.1833 | 206.4166 | 25.533 | 5272.515 |  |  | 3:00 | 180.6775 | 424.4559 | 2421.9736 | 176.3987 | 0.29268 | 1.7487 | 81.1833 | 204.6696 | 25.533 | 3516.933
4:00 | 180.6775 | 144.7039 | 0 | 2304.688 | 0.15828 | 21.8898 | 81.1833 | 200.7646 | 18.8138 | 2952.8792 |  |  | 4:00 | 180.6775 | 336.2256 | 0 | 185.0283 | 0.20243 | 1.8342 | 81.1833 | 200.8105 | 18.8138 | 1004.7756
5:00 | 180.6775 | 144.7039 | 0 | 2468.1274 | 0.18566 | 22.8185 | 81.1833 | 213.2419 | 13.4384 | 3124.3766 |  |  | 5:00 | 180.6775 | 336.2256 | 0 | 296.7051 | 0.17475 | 2.9413 | 81.1833 | 208.5809 | 13.4384 | 1119.9269
6:00 | 180.6775 | 144.7039 | 0 | 3390.2058 | 0.34014 | 30.7872 | 81.1833 | 253.9743 | 8.063 | 4089.9353 |  |  | 6:00 | 180.6775 | 336.2256 | 0 | 503.3074 | 0.16698 | 4.9894 | 81.1833 | 233.9492 | 8.063 | 1348.5624
7:00 | 180.6775 | 144.7039 | 0 | 5361.5965 | 0.67041 | 50.2676 | 81.1833 | 322.9072 | 17.4699 | 6159.4762 |  |  | 7:00 | 180.6775 | 336.2256 | 0 | 531.4804 | 0.23381 | 5.2687 | 81.1833 | 283.302 | 17.4699 | 1435.8413
8:00 | 180.6775 | 186.446 | 2421.9736 | 6633.4289 | 0.80033 | 62.7577 | 81.1833 | 359.4094 | 29.5645 | 9956.2413 |  |  | 8:00 | 180.6775 | 424.4559 | 2421.9736 | 569.8059 | 0.38191 | 5.6486 | 81.1833 | 347.1998 | 29.5645 | 4060.891
9:00 | 180.6775 | 186.446 | 2421.9736 | 7150.7263 | 0.887 | 67.8344 | 81.1833 | 376.9609 | 41.659 | 10508.3481 |  |  | 9:00 | 180.6775 | 424.4559 | 2421.9736 | 586.5574 | 0.43854 | 5.8147 | 81.1833 | 393.9319 | 41.659 | 4136.6919
10:00 | 180.6775 | 186.446 | 2421.9736 | 6682.5262 | 0.80856 | 63.6517 | 81.1833 | 381.2817 | 34.9398 | 10033.4885 |  |  | 10:00 | 180.6775 | 424.4559 | 2421.9736 | 509.3988 | 0.49674 | 5.0498 | 81.1833 | 402.8935 | 34.9398 | 4061.069
11:00 | 181.2524 | 186.446 | 2421.9736 | 6073.7285 | 0.70656 | 57.5402 | 81.1833 | 370.5403 | 28.2206 | 9401.5917 |  |  | 11:00 | 181.2524 | 424.4559 | 2421.9736 | 509.9065 | 0.55741 | 5.0548 | 81.1833 | 407.6655 | 28.2206 | 4060.2701
12:00 | 181.2524 | 186.446 | 2421.9736 | 5932.8588 | 0.68296 | 56.0382 | 81.1833 | 365.423 | 22.8453 | 9248.7037 |  |  | 12:00 | 181.2524 | 424.4559 | 2421.9736 | 523.6123 | 0.58875 | 5.1907 | 81.1833 | 415.1209 | 22.8453 | 4076.2232
13:00 | 181.2524 | 186.446 | 2421.9736 | 5763.9488 | 0.65466 | 54.7799 | 81.1833 | 367.7989 | 25.533 | 9083.5707 |  |  | 13:00 | 181.2524 | 424.4559 | 2421.9736 | 457.6214 | 0.65286 | 4.5365 | 81.1833 | 404.346 | 25.533 | 4001.555
14:00 | 181.2524 | 186.446 | 2421.9736 | 5833.7454 | 0.66636 | 55.8709 | 81.1833 | 360.3372 | 24.1891 | 9145.6643 |  |  | 14:00 | 181.2524 | 424.4559 | 2421.9736 | 400.0063 | 0.70188 | 3.9654 | 81.1833 | 401.2686 | 24.1891 | 3938.9964
15:00 | 181.2524 | 186.446 | 2421.9736 | 6015.3242 | 0.69678 | 57.416 | 81.1833 | 359.8236 | 24.1891 | 9328.305 |  |  | 15:00 | 181.2524 | 424.4559 | 2421.9736 | 440.8698 | 0.70912 | 4.3705 | 81.1833 | 405.8541 | 24.1891 | 3984.8579
16:00 | 181.2524 | 144.7039 | 0 | 6202.8541 | 0.81135 | 58.2931 | 81.1833 | 365.2218 | 26.8768 | 7061.1967 |  |  | 16:00 | 181.2524 | 336.2256 | 0 | 593.1565 | 0.57892 | 5.8801 | 81.1833 | 450.9235 | 26.8768 | 1676.0771
17:00 | 181.2524 | 144.7039 | 0 | 7250.3866 | 0.98685 | 66.8436 | 81.1833 | 406.2677 | 14.4721 | 8146.0965 |  |  | 17:00 | 181.2524 | 336.2256 | 0 | 903.0598 | 0.47173 | 8.9523 | 81.1833 | 542.3265 | 14.4721 | 2067.9437
18:00 | 181.2524 | 144.7039 | 0 | 8020.833 | 1.1159 | 74.5618 | 81.1833 | 522.6252 | 40.3152 | 9066.5907 |  |  | 18:00 | 181.2524 | 336.2256 | 0 | 897.2222 | 0.46015 | 8.8944 | 81.1833 | 542.0794 | 40.3152 | 2087.6326
19:00 | 181.2524 | 144.7039 | 0 | 7318.8743 | 0.99832 | 68.4776 | 81.1833 | 530.3969 | 52.4098 | 8378.2964 |  |  | 19:00 | 181.2524 | 336.2256 | 0 | 747.7274 | 0.13598 | 7.4124 | 81.1833 | 505.6715 | 52.4098 | 1912.0184
20:00 | 181.2524 | 186.446 | 2421.9736 | 6864.035 | 0.83897 | 64.6292 | 81.1833 | 502.0107 | 48.3782 | 10350.7474 |  |  | 20:00 | 181.2524 | 424.4559 | 2421.9736 | 637.3196 | 0.23669 | 6.3179 | 81.1833 | 465.7749 | 48.3782 | 4266.8927
21:00 | 181.2524 | 186.446 | 2421.9736 | 6183.9141 | 0.72502 | 58.4914 | 81.1833 | 461.4897 | 44.3467 | 9619.8224 |  |  | 21:00 | 181.2524 | 424.4559 | 2421.9736 | 533.2571 | 0.24854 | 5.2863 | 81.1833 | 416.2452 | 44.3467 | 4108.2491
22:00 | 181.2524 | 186.446 | 2421.9736 | 4975.4315 | 0.52256 | 46.9373 | 81.1833 | 424.7429 | 40.3152 | 8358.8048 |  |  | 22:00 | 181.2524 | 424.4559 | 2421.9736 | 447.9766 | 0.26721 | 4.4409 | 81.1833 | 384.2443 | 40.3152 | 3986.1094
23:00 | 181.2524 | 186.446 | 2421.9736 | 3598.2552 | 0.29184 | 34.0371 | 81.1833 | 379.8485 | 43.0029 | 6926.291 |  |  | 23:00 | 181.2524 | 424.4559 | 2421.9736 | 309.9033 | 0.29732 | 3.0722 | 81.1833 | 340.0549 | 43.0029 | 3805.1958
Heat balance | [12 empty] | Heat balance
| Heat demand | Qlosses grid total | VF produce (Qhe3) | Central HP2 Win | ATES | NBH cooling | Total supply | Tot demand | [5 empty] | Heat demand | Losses grid | VF produce | Central HP2 Win | ATES | NBH cooling | Total supply | Tot demand
| kW | kW | kW | kW | kW | kW | kW | kW | [5 empty] | kW | kW | kW | kW | kW | kW | kW | kW
0:00 | 4994.7943 | 1246.4798 | 2366.2223 | 2428.9427 | 898.8127 | 547.2963 | 6241.2741 | 6241.2741 |  |  |  |  | 0:00 | 558.3164 | 148.153 | 2604.2321 | 212.6937 | -2657.7528 | 547.2963 | 706.4694 | 706.4694
1:00 | 4153.1777 | 1036.4495 | 2366.2223 | 2019.6689 | 256.4396 | 547.2963 | 5189.6271 | 5189.6271 |  |  |  |  | 1:00 | 452.3828 | 120.0428 | 2604.2321 | 172.3377 | -2751.4405 | 547.2963 | 572.4257 | 572.4257
2:00 | 4108.2412 | 1025.2353 | 2366.2223 | 1997.8165 | 222.1414 | 547.2963 | 5133.4765 | 5133.4765 |  |  |  |  | 2:00 | 455.0478 | 120.75 | 2604.2321 | 173.353 | -2749.0836 | 547.2963 | 575.7978 | 575.7978
3:00 | 4420.8611 | 1103.2514 | 2366.2223 | 2149.8419 | 460.7519 | 547.2963 | 5524.1125 | 5524.1125 |  |  |  |  | 3:00 | 463.0428 | 122.8715 | 2604.2321 | 176.3987 | -2742.0128 | 547.2963 | 585.9143 | 585.9143
4:00 | 4739.2813 | 1182.715 | 1587.182 | 2304.688 | 1482.8299 | 547.2963 | 5921.9963 | 5921.9963 |  |  |  |  | 4:00 | 485.6953 | 128.8825 | 1778.7037 | 185.0283 | -1896.4505 | 547.2963 | 614.5778 | 614.5778
5:00 | 5075.3724 | 1266.5885 | 1587.182 | 2468.1274 | 1739.3552 | 547.2963 | 6341.9609 | 6341.9609 |  |  |  |  | 5:00 | 778.8447 | 206.6716 | 1778.7037 | 296.7051 | -1637.1888 | 547.2963 | 985.5163 | 985.5163
6:00 | 6971.5028 | 1739.7788 | 1587.182 | 3390.2058 | 3186.5974 | 547.2963 | 8711.2816 | 8711.2816 |  |  |  |  | 6:00 | 1321.1711 | 350.5816 | 1778.7037 | 503.3074 | -1564.3446 | 954.0862 | 1671.7527 | 1671.7527
7:00 | 11025.4028 | 2751.4529 | 1587.182 | 5361.5965 | 6280.7809 | 547.2963 | 13776.8557 | 13776.8557 |  |  |  |  | 7:00 | 1395.1247 | 370.2057 | 1778.7037 | 531.4804 | -2190.4828 | 1645.629 | 1765.3304 | 1765.3304
8:00 | 13640.7552 | 3404.1292 | 2366.2223 | 6633.4289 | 7497.937 | 547.2963 | 17044.8845 | 17044.8845 |  |  |  |  | 8:00 | 1495.7283 | 396.9015 | 2604.2321 | 569.8059 | -3577.9011 | 2296.4929 | 1892.6297 | 1892.6297
9:00 | 14704.5079 | 3669.5948 | 2366.2223 | 7150.7263 | 8309.8578 | 547.2963 | 18374.1027 | 18374.1027 |  |  |  |  | 9:00 | 1539.7007 | 408.5699 | 2604.2321 | 586.5574 | -4108.5178 | 2865.9987 | 1948.2705 | 1948.2705
10:00 | 13741.7172 | 3429.3249 | 2366.2223 | 6682.5262 | 7574.9973 | 547.2963 | 17171.0421 | 17171.0421 |  |  |  |  | 10:00 | 1337.1611 | 354.8246 | 2604.2321 | 509.3988 | -4653.7549 | 3232.1097 | 1691.9857 | 1691.9857
11:00 | 12489.8067 | 3116.9034 | 2366.2223 | 6073.7285 | 6619.4629 | 547.2963 | 15606.71 | 15606.71 |  |  |  |  | 11:00 | 1338.4936 | 355.1782 | 2604.2321 | 509.9065 | -5222.0823 | 3801.6155 | 1693.6718 | 1693.6718
12:00 | 12200.1271 | 3044.6122 | 2366.2223 | 5932.8588 | 6398.3618 | 547.2963 | 15244.7392 | 15244.7392 |  |  |  |  | 12:00 | 1374.471 | 364.7251 | 2604.2321 | 523.6123 | -5515.6958 | 4127.0474 | 1739.1961 | 1739.1961
13:00 | 11852.7863 | 2957.9313 | 2366.2223 | 5763.9488 | 6133.2501 | 547.2963 | 14810.7176 | 14810.7176 |  |  |  |  | 13:00 | 1201.2463 | 318.7587 | 2604.2321 | 457.6214 | -6116.3647 | 4574.5163 | 1520.0051 | 1520.0051
14:00 | 11996.3136 | 2993.7493 | 2366.2223 | 5833.7454 | 6242.7989 | 547.2963 | 14990.0629 | 14990.0629 |  |  |  |  | 14:00 | 1050.0079 | 278.6266 | 2604.2321 | 400.0063 | -6575.5521 | 4899.9482 | 1328.6345 | 1328.6345
15:00 | 12369.706 | 3086.9316 | 2366.2223 | 6015.3242 | 6527.7947 | 547.2963 | 15456.6376 | 15456.6376 |  |  |  |  | 15:00 | 1157.2739 | 307.0904 | 2604.2321 | 440.8698 | -6643.4019 | 5062.6642 | 1464.3643 | 1464.3643
16:00 | 12755.3361 | 3183.1678 | 1587.182 | 6202.8541 | 7601.1714 | 547.2963 | 15938.5038 | 15938.5038 |  |  |  |  | 16:00 | 1557.0231 | 413.1665 | 1778.7037 | 593.1565 | -5423.6558 | 5021.9852 | 1970.1896 | 1970.1896
17:00 | 14909.4459 | 3720.7383 | 1587.182 | 7250.3866 | 9245.3193 | 547.2963 | 18630.1843 | 18630.1843 |  |  |  |  | 17:00 | 2370.5128 | 629.0314 | 1778.7037 | 903.0598 | -4419.4517 | 4737.2323 | 2999.5442 | 2999.5442
18:00 | 16493.7653 | 4116.1144 | 1587.182 | 8020.833 | 10454.5684 | 547.2963 | 20609.8797 | 20609.8797 |  |  |  |  | 18:00 | 2355.189 | 624.9651 | 1778.7037 | 897.2222 | -4310.967 | 4615.1953 | 2980.1542 | 2980.1542
19:00 | 15050.2816 | 3755.8847 | 1587.182 | 7318.8743 | 9352.8136 | 547.2963 | 18806.1663 | 18806.1663 |  |  |  |  | 19:00 | 1962.7686 | 520.8338 | 1778.7037 | 747.7274 | -1273.8958 | 1231.067 | 2483.6023 | 2483.6023
20:00 | 14114.9657 | 3522.4712 | 2366.2223 | 6864.035 | 7859.8833 | 547.2963 | 17637.4369 | 17637.4369 |  |  |  |  | 20:00 | 1672.9504 | 443.9286 | 2604.2321 | 637.3196 | -2217.4491 | 1092.7763 | 2116.879 | 2116.879
21:00 | 12716.3885 | 3173.4482 | 2366.2223 | 6183.9141 | 6792.404 | 547.2963 | 15889.8367 | 15889.8367 |  |  |  |  | 21:00 | 1399.7885 | 371.4432 | 2604.2321 | 533.2571 | -2328.4259 | 962.1684 | 1771.2317 | 1771.2317
22:00 | 10231.3063 | 2553.2816 | 2366.2223 | 4975.4315 | 4895.6378 | 547.2963 | 12784.5879 | 12784.5879 |  |  |  |  | 22:00 | 1175.9289 | 312.0406 | 2604.2321 | 447.9766 | -2503.3592 | 939.12 | 1487.9695 | 1487.9695
23:00 | 7399.3284 | 1846.5451 | 2366.2223 | 3598.2552 | 2734.0997 | 547.2963 | 9245.8735 | 9245.8735 |  |  |  |  | 23:00 | 813.4896 | 215.8649 | 2604.2321 | 309.9033 | -2785.4868 | 900.7059 | 1029.3545 | 1029.3545
Cold balance | [12 empty] | Cold balance
| VF demand (incl Win) | NBH cooling (HP3) | Central HP2 cold production | ATES | Heat gains grid | Total supply | Total demand | [6 empty] | VF demand (incl Win) | NBH cooling | Central HP2 cold production | ATES | Heat gains grid | Total supply | Total demand
| kW | kW | kW | kW | kW | kW | kW | [6 empty] | kW | kW | kW | kW | kW | kW | kW
0:00 | 2366.2223 | 547.2963 | 3315.0708 | -898.8127 | 497.2606 | 2913.5186 | 2913.5186 | [5 empty] | 0:00 | 2604.2321 | 547.2963 | 429.3702 | 2657.7528 | 64.4055 | 3151.5285 | 3151.5285
1:00 | 2366.2223 | 547.2963 | 2756.4854 | -256.4396 | 413.4728 | 2913.5186 | 2913.5186 | [5 empty] | 1:00 | 2604.2321 | 547.2963 | 347.9026 | 2751.4405 | 52.1854 | 3151.5285 | 3151.5285
2:00 | 2366.2223 | 547.2963 | 2726.6609 | -222.1414 | 408.9991 | 2913.5186 | 2913.5186 | [5 empty] | 2:00 | 2604.2321 | 547.2963 | 349.9521 | 2749.0836 | 52.4928 | 3151.5285 | 3151.5285
3:00 | 2366.2223 | 547.2963 | 2934.1483 | -460.7519 | 440.1222 | 2913.5186 | 2913.5186 | [5 empty] | 3:00 | 2604.2321 | 547.2963 | 356.1005 | 2742.0128 | 53.4151 | 3151.5285 | 3151.5285
4:00 | 1587.182 | 547.2963 | 3145.4854 | -1482.8299 | 471.8228 | 2134.4783 | 2134.4783 | [5 empty] | 4:00 | 1778.7037 | 547.2963 | 373.5213 | 1896.4505 | 56.0282 | 2326 | 2326
5:00 | 1587.182 | 547.2963 | 3368.5509 | -1739.3552 | 505.2826 | 2134.4783 | 2134.4783 | [5 empty] | 5:00 | 1778.7037 | 547.2963 | 598.9662 | 1637.1888 | 89.8449 | 2326 | 2326
6:00 | 1587.182 | 547.2963 | 4627.0224 | -3186.5974 | 694.0534 | 2134.4783 | 2134.4783 | [5 empty] | 6:00 | 1778.7037 | 954.0862 | 1016.0394 | 1564.3446 | 152.4059 | 2732.7899 | 2732.7899
7:00 | 1587.182 | 547.2963 | 7317.6167 | -6280.7809 | 1097.6425 | 2134.4783 | 2134.4783 | [5 empty] | 7:00 | 1778.7037 | 1645.629 | 1072.913 | 2190.4828 | 160.937 | 3424.3328 | 3424.3328
8:00 | 2366.2223 | 547.2963 | 9053.4396 | -7497.937 | 1358.0159 | 2913.5186 | 2913.5186 | [5 empty] | 8:00 | 2604.2321 | 2296.4929 | 1150.2816 | 3577.9011 | 172.5422 | 4900.725 | 4900.725
9:00 | 2366.2223 | 547.2963 | 9759.4577 | -8309.8578 | 1463.9187 | 2913.5186 | 2913.5186 | [5 empty] | 9:00 | 2604.2321 | 2865.9987 | 1184.0984 | 4108.5178 | 177.6148 | 5470.2309 | 5470.2309
10:00 | 2366.2223 | 547.2963 | 9120.4486 | -7574.9973 | 1368.0673 | 2913.5186 | 2913.5186 | [5 empty] | 10:00 | 2604.2321 | 3232.1097 | 1028.3364 | 4653.7549 | 154.2505 | 5836.3418 | 5836.3418
11:00 | 2366.2223 | 547.2963 | 8289.5491 | -6619.4629 | 1243.4324 | 2913.5186 | 2913.5186 | [5 empty] | 11:00 | 2604.2321 | 3801.6155 | 1029.3612 | 5222.0823 | 154.4042 | 6405.8477 | 6405.8477
12:00 | 2366.2223 | 547.2963 | 8097.2873 | -6398.3618 | 1214.5931 | 2913.5186 | 2913.5186 | [5 empty] | 12:00 | 2604.2321 | 4127.0474 | 1057.0294 | 5515.6958 | 158.5544 | 6731.2796 | 6731.2796
13:00 | 2366.2223 | 547.2963 | 7866.7555 | -6133.2501 | 1180.0133 | 2913.5186 | 2913.5186 | [5 empty] | 13:00 | 2604.2321 | 4574.5163 | 923.8119 | 6116.3647 | 138.5718 | 7178.7485 | 7178.7485
14:00 | 2366.2223 | 547.2963 | 7962.0153 | -6242.7989 | 1194.3023 | 2913.5186 | 2913.5186 | [5 empty] | 14:00 | 2604.2321 | 4899.9482 | 807.5028 | 6575.5521 | 121.1254 | 7504.1804 | 7504.1804
15:00 | 2366.2223 | 547.2963 | 8209.8377 | -6527.7947 | 1231.4757 | 2913.5186 | 2913.5186 | [5 empty] | 15:00 | 2604.2321 | 5062.6642 | 889.9952 | 6643.4019 | 133.4993 | 7666.8963 | 7666.8963
16:00 | 1587.182 | 547.2963 | 8465.7824 | -7601.1714 | 1269.8674 | 2134.4783 | 2134.4783 | [5 empty] | 16:00 | 1778.7037 | 5021.9852 | 1197.4201 | 5423.6558 | 179.613 | 6800.6889 | 6800.6889
17:00 | 1587.182 | 547.2963 | 9895.4762 | -9245.3193 | 1484.3214 | 2134.4783 | 2134.4783 | [5 empty] | 17:00 | 1778.7037 | 4737.2323 | 1823.0299 | 4419.4517 | 273.4545 | 6515.936 | 6515.936
18:00 | 1587.182 | 547.2963 | 10946.9971 | -10454.5684 | 1642.0496 | 2134.4783 | 2134.4783 | [5 empty] | 18:00 | 1778.7037 | 4615.1953 | 1811.2452 | 4310.967 | 271.6868 | 6393.899 | 6393.899
19:00 | 1587.182 | 547.2963 | 9988.9495 | -9352.8136 | 1498.3424 | 2134.4783 | 2134.4783 | [5 empty] | 19:00 | 1778.7037 | 1231.067 | 1509.4564 | 1273.8958 | 226.4185 | 3009.7707 | 3009.7707
20:00 | 2366.2223 | 547.2963 | 9368.1756 | -7859.8833 | 1405.2263 | 2913.5186 | 2913.5186 | [5 empty] | 20:00 | 2604.2321 | 1092.7763 | 1286.5734 | 2217.4491 | 192.986 | 3697.0084 | 3697.0084
21:00 | 2366.2223 | 547.2963 | 8439.9327 | -6792.404 | 1265.9899 | 2913.5186 | 2913.5186 | [5 empty] | 21:00 | 2604.2321 | 962.1684 | 1076.4996 | 2328.4259 | 161.4749 | 3566.4005 | 3566.4005
22:00 | 2366.2223 | 547.2963 | 6790.5708 | -4895.6378 | 1018.5856 | 2913.5186 | 2913.5186 | [5 empty] | 22:00 | 2604.2321 | 939.12 | 904.3417 | 2503.3592 | 135.6513 | 3543.3521 | 3543.3521
23:00 | 2366.2223 | 547.2963 | 4910.9724 | -2734.0997 | 736.6459 | 2913.5186 | 2913.5186 | [5 empty] | 23:00 | 2604.2321 | 900.7059 | 625.6097 | 2785.4868 | 93.8415 | 3504.938 | 3504.938

## VF_Dec
Vertical farm in decentralised configuration
Winter | [6 empty] | Summer
Photoperiod | [6 empty] | Photoperiod
air/water HE1 (cooling and dehumidification) | [6 empty] | air/water HE1 (cooling and dehumidification)
TOTAL (All HE1) | [6 empty] | TOTAL (All HE1)
Qtot air-side = (h2-h1) * mair | -0.10342 | kJ/s | equal to Qout |  |  |  | Qtot air-side = (h2-h1) * mair | -0.10342 | kJ/s | equal to Qout
Qs air-side | -0.076208 | kJ/s | equal to Qout;s |  |  |  | Qs air-side | -0.076208 | kJ/s | equal to Qout;s
Ql air-side | -0.027211 | kJ/s | equal to Qout;l |  |  |  | Ql air-side | -0.027211 | kJ/s | equal to Qout;l
ma | 0.011234 | kg/s |  |  |  |  | ma | 0.011234 | kg/s
Qt air-side = Qt water-side = Qs water-side | -0.10342 | kJ/s | assumed no heat losses in HE |  |  |  | Qt air-side = Qt water-side = Qs water-side | -0.10342 | kJ/s | assumed no heat losses in HE
Qs = mw * Cpw * dT | [6 empty] | Qs = mw * Cpw * dT
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
mw | -0.0045774 | kg/s |  |  |  |  | mw | -0.0045774 | kg/s
water/air HE | [6 empty] | water/air HE
ε - Effectiveness HE (%) | ε = dT min fluid / dT max HE | [5 empty] | ε - Effectiveness HE (%) | ε = dT min fluid / dT max HE
ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 70% | assumption made for w/a HE counterflow |  |  |  |  | ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 70% | assumption made for w/a HE counterflow
| 70% | [6 empty] | 70%
Tc,i = Tw,i | 16.73 | C | see formulae below |  |  |  | Tc,i = Tw,i | 16.73 | C | see formulae below
Tc,o = Tw,o | 22.13 | C | see evaporator |  |  |  | Tc,o = Tw,o | 22.13 | C | see evaporator
Th,i= Ta,i | 26 | C |  |  |  |  | Th,i= Ta,i | 26 | C
Th,o = Ta,o | 19.511 | C |  |  |  |  | Th,o = Ta,o | 19.511 | C
the formulae above agrees with the formulae below from Mansour & Fath 2016 (http://dx.doi.org/10.1016/j.desal.2016.05.025) | [6 empty] | the formulae above agrees with the formulae below from Mansour & Fath 2016 (http://dx.doi.org/10.1016/j.desal.2016.05.025)
| in which | [6 empty] | in which
| Tao = Tair,out | [6 empty] | Tao = Tair,out
| Tai = Tair, in | [6 empty] | Tai = Tair, in
| Twin = Twater, in | [6 empty] | Twin = Twater, in
air/water HE2 (heating) | [6 empty] | air/water HE2 (heating)
Qhe = ma * (h3-h2) | 0.05199 | kJ/s | equal to Qin |  |  |  | Qhe = ma * (h3-h2) | 0.05199 | kJ/s | equal to Qin
Qs = mw * Cpw * dT | [6 empty] | Qs = mw * Cpw * dT
mw | 0.0027681 | kg/s |  |  |  |  | mw | 0.0027681 | kg/s
ε = Qactual / Qmax | 70% | [5 empty] | ε = Qactual / Qmax | 70%
ε = (Th,o - Th,I) / (Th,i - Tc,i) | [6 empty] | ε = (Th,o - Th,I) / (Th,i - Tc,i)
Tc,i | 19.511 | C |  |  |  |  | Tc,i | 19.511 | C
Tc,o | 24 | C |  |  |  |  | Tc,o | 24 | C
Th,i | 25.9239 | C |  |  |  |  | Th,i | 25.9239 | C
Th,o | 21.4349 | C |  |  |  |  | Th,o | 21.4349 | C
Qs air-side =- Qs water-side | 0.05199 | kJ/s | as no heat losses assumed |  |  |  | Qs air-side =- Qs water-side | 0.05199 | kJ/s | as no heat losses assumed
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
HE3 and valve 3 | [6 empty] | HE3 and valve 3
HE3 | [6 empty] | HE3
Qhe3= mw4b * Cw * dT | [6 empty] | Qhe3= mw4b * Cw * dT
Qhe3 = Qcon - Qhe2 | 0.055827 | kJ/s | 326.0325 | kWh m-2 y-1 | 55.8275 | W m-2 | Qhe3 = Qcon - Qhe2 | 0.061443 | kJ/s | 358.827 | kWh m-2 y-1 | 61.443 | W m-2
water/water HE | [6 empty] | water/water HE
ε - Effectiveness HE (%) | 80% | [5 empty] | ε - Effectiveness HE (%) | 80%
Tc,i (connection LT DHN cold) | 2.75 | C |  |  |  |  | Tc,i (connection LT DHN cold) | 11.25 | C
Tc,o (connection LT DHN hot) | 19.75 | C |  |  |  |  | Tc,o (connection LT DHN hot) | 28.25 | C
Th,i | 24 | C |  |  |  |  | Th,i | 32.5 | C
Th,o | 7 | C |  |  |  |  | Th,o | 15.5 | C
Qs air-side =- Qs water-side | 55.8275 | J/s | as no heat losses |  |  |  | Qs air-side =- Qs water-side | 61.443 | J/s | as no heat losses
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
mw2c | -0.00078489 | kg/s |  |  |  |  | mw2c | -0.00086384 | kg/s
ma 2 | 0.0032676 | kg/s |  |  |  |  | ma 2 | 0.0035963 | kg/s
valve 3 | [6 empty] | valve 3
ml = (Th - Tf) / (Th - Tl) * mf | [6 empty] | ml = (Th - Tf) / (Th - Tl) * mf
ml = mass flow low temperature in | 0.00078489 | kg/s |  |  |  |  | ml = mass flow low temperature in | 0.00086384 | kg/s
tl = low temperature in | 7 | C |  |  |  |  | tl = low temperature in | 15.5 | C
th | 24 | C |  |  |  |  | th | 32.5 | C
mf | 0.0027681 | kg/s |  |  |  |  | mf | 0.0027681 | kg/s
tf | 25.9239 | C |  |  |  |  | tf | 25.9239 | C
mh = mf - ml | 0.0019832 | kg/s |  |  |  |  | mh = mf - ml | 0.0019043 | kg/s
water-water heat pump HP1 | [6 empty] | water-water heat pump HP1
Q = mw * Cpw * dT | 0.10782 | kJ/s |  |  |  |  | Q = mw * Cpw * dT | 0.11343 | kJ/s
ε | 90% | [5 empty] | ε | 90%
Tc,i | 21.4349 | C |  |  |  |  | Tc,i | 21.4349 | C
Tc,o | 24 | C |  |  |  |  | Tc,o | 32.5 | C
Th,i = Th,o = Tcon = T1 | 24.285 | C |  |  |  |  | Th,i = Th,o = Tcon = T1 | 33.7295
TD = Th - Tc,i | 2.8502 | [5 empty] | TD = Th - Tc,i | 12.2946
Evaporator | [6 empty] | Evaporator
Qhot = mh * Ch * dT | -0.10342 | kJ/s |  |  |  |  | Qhot = mh * Ch * dT | -0.10342 | kJ/s
Qcold | 0.10342 | kJ/s |  |  |  |  | Qcold | 0.10342 | kJ/s
Simplified | [6 empty] | Simplified
E = Qa / Qmax | [6 empty] | E = Qa / Qmax
E = Cw * Cpw * (Th,o - Th,i) / Cmin * (Th,o - Tc) | [6 empty] | E = Cw * Cpw * (Th,o - Th,i) / Cmin * (Th,o - Tc)
Cmin = Cw * Cpw as Cref = infinite | [6 empty] | Cmin = Cw * Cpw as Cref = infinite
Thus, e = (Th,i - Th,o) / (Th,i - Tc) | 90% | [5 empty] | Thus, e = (Th,i - Th,o) / (Th,i - Tc) | 90%
Th,i = Thot in | 22.13 | C |  |  |  |  | Th,i = Thot in | 22.13 | C
Th,o = Thot, out | 16.73 | C |  |  |  |  | Th,o = Thot, out | 16.73 | C
Tc,i = Tc, o = T3 | 16.13 | C |  |  |  |  | Tc,i = Tc, o = T3 | 16.13 | C
TD = Th,i - Tc | 6 | C |  |  |  |  | TD = Th,i - Tc | 6 | C
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K) |  |  | Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 24.285 | 6.5233 | 233.62 |  |  |  | 1 - Saturated liquid (100%): subcooling | 33.7295 | 8.5707 | 247.25
2 - liquid + vapour | 16.13 | 5.0631 | 233.62 |  |  |  | 2 - liquid + vapour | 16.13 | 5.0631 | 247.25
3 - Saturated vapour (100%): superheat | 16.13 | 5.0631 | 407.86 | 1.7204 |  |  | 3 - Saturated vapour (100%): superheat | 16.13 | 5.0631 | 407.86 | 1.7204
4 -liquid + vapour: highly superheated | 25.0479 | 6.5233 | 413.0479 | 1.7204 |  |  | 4 -liquid + vapour: highly superheated | 35.4829 | 8.5707 | 418.7467 | 1.7204
[7 empty] | 4 calculated with P-bar 850 | 35.1647 |  | 418.5746
[7 empty] | 4 calculated with P-base 900 | 37.4154 |  | 419.7919
[7 empty] | percentage | 0.14138
Isentropic efficiency | [6 empty] | Isentropic efficiency
E | 0.7 | [5 empty] | E | 0.7
E = (h4 - h3) / (h4' - h3) | [6 empty] | E = (h4 - h3) / (h4' - h3)
h4' | 415.2713 | kJ/kg |  |  |  |  | h4' | 423.4124 | kJ/kg
Qcold = Qev | [6 empty] | Qcold = Qev
Qcold = m * (h3-h2) | -0.10342 | kJ/s | sensible and latent heat |  |  |  | Qcold = m * (h3-h2) | -0.10342 | kJ/s | sensible and latent heat
ṁr = flow rate refrigerant | -0.00059354 | kg/s |  |  |  |  | ṁr = flow rate refrigerant | -0.00064391 | kg/s
ṁ water through evaporator | 0.0045774 | kg/s |  |  |  |  | ṁ water through evaporator | 0.0045774 | kg/s
Qhot = Qcon | [6 empty] | Qhot = Qcon
Q = mw * Cpw * dT | 107.8178 | J/s |  |  |  |  | Q = mw * Cpw * dT | 113.4332 | J/s
mw = mf | 0.010046 | kg/s |  |  |  |  | mw = mf | 0.0024501 | kg/s
Qhot = mr * (h1-h4') | 0.10782 | kJ/s |  |  |  |  | Qhot = mr * (h1-h4') | 0.11343 | kJ/s
ṁr = flow rate refrigerant | -0.00059354 | kg/s |  |  |  |  | ṁr = flow rate refrigerant | -0.00064391 | kg/s
COP cooling | [6 empty] | COP cooling
COPhp = (h4'-h1)/(h4'-h3) | 24.5101 | [5 empty] | COPhp = (h4'-h1)/(h4'-h3) | 11.327
Win = Qcon / COPhp | 0.0043989 | kJ/s |  |  |  |  | Win = Qcon / COPhp | 0.010014 | kJ/s
Win = m *dh | 0.0043989 | kJ/s |  |  |  |  | Win = m *dh | 0.010014 | kJ/s
COPref = (h3-h2) / (h4' - h3) | 23.5101 | [5 empty] | COPref = (h3-h2) / (h4' - h3) | 10.327
Win = Qev / COPref | 0.0043989 | kJ/s |  |  |  |  | Win = Qev / COPref | 0.010014 | kJ/s
Total energy use VF | [6 empty] | Total energy use VF
Energy use pumps | [6 empty] | Energy use pumps
Epump (kW) = (dp * Capacity) /( 36 * n ) | [6 empty] | Epump (kW) = (dp * Capacity) /( 36 * n )
dp pressure difference [bar] | [6 empty] | dp pressure difference [bar]
Capacity in m3/h | [6 empty] | Capacity in m3/h
n pumping system optimized | 72% |  | Kaya et al., 2021 |  |  |  | n pumping system optimized | 72% |  | Kaya et al., 2021
Pressure (bar), P = 0,981 * h * SG | [6 empty] | Pressure (bar), P = 0,981 * h * SG
SG specific gravity fluid, for water | 1 | [5 empty] | SG specific gravity fluid, for water | 1
head = height difference between the fluid being moved and the discharge point (m) |  |  | 1 |  |  |  | head = height difference between the fluid being moved and the discharge point (m) |  |  | 1
| unit | Pump HE1-Ev | Pump HE2 - con | Total |  |  |  | unit | Pump HE1-Ev | Pump HE2 - con | Total
Head | m | 1 | 1 |  |  |  | Head | m | 1 | 1
dP (average pressure difference) | bar | 0.098 | 0.098 |  |  |  | dP (average pressure difference) | bar | 0.098 | 0.098
flow rate | kg/s | 0.0045774 | 0.0027681 |  |  |  | flow rate | kg/s | 0.0045774 | 0.0027681
Capacity | m3/s | 4.5911e-06 | 2.7764e-06 |  |  |  | Capacity | m3/s | 4.5911e-06 | 2.7764e-06
Capacity | m3/h | 0.016528 | 0.0099951 |  |  |  | Capacity | m3/h | 0.016528 | 0.0099951
n pump | % | 72% | 72% |  |  |  | n pump | % | 72% | 72%
Epump | W | 0.06249 | 0.03779 |  |  |  | Epump | W | 0.06249 | 0.03779
Epump | kWh m-2 d-1 | 0.00099984 | 0.00060464 | 0.0016045 |  |  | Epump | kWh m-2 d-1 | 0.00099984 | 0.00060464 | 0.0016045
velocity water pipes | m/s | 2 | 2 |  |  |  | velocity water pipes | m/s | 2 | 2
p water | 997 | kg/m3 |  |  |  |  | p water | 997 | kg/m3
h active (day) | 16 | hrs/yr |  |  |  |  | h active (day) | 16 | hrs/yr
Energy use fans | [6 empty] | Energy use fans
Calculations based on Graamans et al., 2020 | [6 empty] | Calculations based on Graamans et al., 2020
Including assumptions fan efficiency 65% and Uair,max 15 m/s | [6 empty] | Including assumptions fan efficiency 65% and Uair,max 15 m/s
| unit | Indoor fan VF | [5 empty] | unit | Indoor fan VF
Air density | kg/m3 | 1.225 |  |  |  |  | Air density | kg/m3 | 1.225
Uair ducts (not farm) | m/s max | 8 |  |  |  |  | Uair ducts (not farm) | m/s max | 8
Friction loss | Pa | 256.8 |  |  |  |  | Friction loss | Pa | 256.8
Pressure difference | Pa | 296 |  |  |  |  | Pressure difference | Pa | 296
Vair | kg/s | 0.011234 |  |  |  |  | Vair | kg/s | 0.011234
Vair | m3/s | 0.0091705 |  |  |  |  | Vair | m3/s | 0.0091705
Vair | m3/h | 33.0138 |  |  |  |  | Vair | m3/h | 33.0138
n fan | % | 65% |  |  |  |  | n fan | % | 65%
E fan | kW | 0.0041761 |  |  |  |  | E fan | kW | 0.0041761
E fan | kWh d-1 | 0.066818 |  |  |  |  | E fan | kWh d-1 | 0.066818
velocity | m/s | 8 |  |  |  |  | velocity | m/s | 8
p air | 1.225 | kg/m3 |  |  |  |  | p air | 1.225 | kg/m3
Total energy use photoperiod (winter) | [6 empty] | Total energy use photoperiod (summer)
Etotal | J m-2 s-1 | J s-1 | kWh m-2 d-1 | kWh d-1 decentralised |  |  | Etotal | J m-2 s-1 | J s-1 | kWh m-2 d-1 | kWh d-1 decentralised
E HP | 4.3989 | 169562.9204 | 0.070383 | 2713.0067 |  |  | E HP | 10.0144 | 386020.4195 | 0.16023 | 6176.3267
Epump | 0.10028 | 3865.4645 | 0.0016045 | 61.8474 |  |  | Epump | 0.10028 | 3865.4645 | 0.0016045 | 61.8474
Efans | 4.1761 | 160974.1492 | 0.066818 | 2575.5864 |  |  | Efans | 4.1761 | 160974.1492 | 0.066818 | 2575.5864
ELED | 57.1429 | 2202658.4092 | 0.91429 | 35242.5345 |  |  | ELED | 57.1429 | 2202658.4092 | 0.91429 | 35242.5345
Etot | 65.8182 | 2537060.9433 | 1.0531 | 40592.9751 |  |  | Etot | 71.4336 | 2753518.4425 | 1.1429 | 44056.2951
Dark period | [6 empty] | Dark period
air/water HE1 (cooling and dehumidification) | [6 empty] | air/water HE1 (cooling and dehumidification)
TOTAL (All HE1) | [6 empty] | TOTAL (All HE1)
Qtot air-side = (h2-h1) * mair | -0.082546 | kJ/s | equal to Qout |  |  |  | Qtot air-side = (h2-h1) * mair | -0.082546 | kJ/s | equal to Qout
Qs air-side | -0.048513 | kJ/s | equal to Qout;s |  |  |  | Qs air-side | -0.048513 | kJ/s | equal to Qout;s
Ql air-side | -0.034033 | kJ/s | equal to Qout;l |  |  |  | Ql air-side | -0.034033 | kJ/s | equal to Qout;l
ma | 0.011234 | kg/s |  |  |  |  | ma | 0.011234 | kg/s
Qt air-side = Qt water-side = Qs water-side | -0.082546 | kJ/s | assumed no heat losses in HE |  |  |  | Qt air-side = Qt water-side = Qs water-side | -0.082546 | kJ/s | assumed no heat losses in HE
Qs = mw * Cpw * dT | [6 empty] | Qs = mw * Cpw * dT
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
mw | -0.0036535 | kg/s |  |  |  |  | mw | -0.0036535 | kg/s
water/air HE | [6 empty] | water/air HE
ε - Effectiveness HE (%) | ε = dT min fluid / dT max HE | [5 empty] | ε - Effectiveness HE (%) | ε = dT min fluid / dT max HE
ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 70% | assumption made for w/a HE counterflow |  |  |  |  | ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 70% | assumption made for w/a HE counterflow
| 70% | [6 empty] | 70%
Tc,i = Tw,i | 16.8614 | C |  |  |  |  | Tc,i = Tw,i | 16.8614 | C
Tc,o = Tw,o | 22.2614 | C |  |  |  |  | Tc,o = Tw,o | 22.2614 | C
Th,i= Ta,i | 23 | C |  |  |  |  | Th,i= Ta,i | 23 | C
Th,o = Ta,o | 18.703 | C |  |  |  |  | Th,o = Ta,o | 18.703 | C
air/water HE2 (heating) | [6 empty] | air/water HE2 (heating)
Qhe = ma * (h3-h2) | 0.048513 | kJ/s | equal to Qin |  |  |  | Qhe = ma * (h3-h2) | 0.048513 | kJ/s | equal to Qin
Qs = mw * Cpw * dT | [6 empty] | Qs = mw * Cpw * dT
mw | 0.0026984 | kg/s |  |  |  |  | mw | 0.0026984 | kg/s
ε = Qactual / Qmax | 70% | [5 empty] | ε = Qactual / Qmax | 70%
Tc,i | 18.703 | C |  |  |  |  | Tc,i | 18.703 | C
Tc,o | 23 | C |  |  |  |  | Tc,o | 23 | C
Th,i | 24.8416 | C |  |  |  |  | Th,i | 24.8416 | C
Th,o | 20.5446 | C |  |  |  |  | Th,o | 20.5446 | C
Qs air-side =- Qs water-side | 0.048513 | kJ/s | as no heat losses assumed |  |  |  | Qs air-side =- Qs water-side | 0.048513 | kJ/s | as no heat losses assumed
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
HE3 and valve 3 | [6 empty] | HE3 and valve 3
HE3 | [6 empty] | HE3
Qhe3= mw4b * Cw * dT | [6 empty] | Qhe3= mw4b * Cw * dT
Qhe3 = Qcon - Qhe2 | 0.037447 | kJ/s | 109.3458 | kWh m-2 y-1 | 37.4472 | W m-2 | Qhe3 = Qcon - Qhe2 | 0.041966 | kJ/s | 122.5403 | kWh m-2 y-1 | 41.9659 | W m-2
water/water HE | [6 empty] | water/water HE
ε - Effectiveness HE (%) | 80% | [5 empty] | ε - Effectiveness HE (%) | 80%
Tc,i (connection LT DHN cold) | 2.75 | C |  |  |  |  | Tc,i (connection LT DHN cold) | 11.25 | C
Tc,o (connection LT DHN hot) | 19.75 | C |  |  |  |  | Tc,o (connection LT DHN hot) | 28.25 | C
Th,i | 24 | C |  |  |  |  | Th,i | 32.5 | C
Th,o | 7 | C |  |  |  |  | Th,o | 15.5 | C
Qs air-side =- Qs water-side | 37.4472 | J/s | as no heat losses |  |  |  | Qs air-side =- Qs water-side | 41.9659 | J/s | as no heat losses
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
mw2c | -0.00052648 | kg/s |  |  |  |  | mw2c | -0.00059 | kg/s
ma 2 | 0.0021918 | kg/s |  |  |  |  | ma 2 | 0.0024563 | kg/s
valve 3 | [6 empty] | valve 3
ml = (Th - Tf) / (Th - Tl) * mf | [6 empty] | ml = (Th - Tf) / (Th - Tl) * mf
ml = mass flow low temperature in | 0.00052648 | kg/s |  |  |  |  | ml = mass flow low temperature in | 0.00059 | kg/s
tl = low temperature in | 7 | C |  |  |  |  | tl = low temperature in | 15.5 | C
th | 24 | C |  |  |  |  | th | 32.5 | C
mf | 0.0026984 | kg/s |  |  |  |  | mf | 0.0026984 | kg/s
tf | 24.8416 | C |  |  |  |  | tf | 24.8416 | C
mh = mf - ml | 0.0021719 | kg/s |  |  |  |  | mh = mf - ml | 0.0021084 | kg/s
water-water heat pump HP1 | [6 empty] | water-water heat pump HP1
Condenser | [6 empty] | Condenser
ε = 1 - EXP (-NTU) | 90% | [5 empty] | ε = 1 - EXP (-NTU) | 90%
(- EXP (-NTU)) | -10% | [5 empty] | (- EXP (-NTU)) | -10%
NTU | 2.3026 | [5 empty] | NTU | 2.3026
Q = mw * Cpw * dT | 0.08596 | kJ/s |  |  |  |  | Q = mw * Cpw * dT | 0.090479 | kJ/s
ε | 90% | [5 empty] | ε | 90%
Tc,i | 20.5446 | C |  |  |  |  | Tc,i | 20.5446 | C
Tc,o | 24 | C |  |  |  |  | Tc,o | 32.5 | C
Th,i = Th,o = Tcon = T1 | 24.3839 | C | selected |  |  |  | Th,i = Th,o = Tcon = T1 | 33.8284 | C | selected |  | T1 > T2 (=T3)
TD = Th - Tc,i | 3.8394 |  | COND: TD water about 8K (RVO) |  |  |  | TD = Th - Tc,i | 13.2838 |  | COND: TD water about 8K (RVO)
Simplified | [6 empty] | Simplified
E = Qa / Qmax | [6 empty] | E = Qa / Qmax
E = Cw * Cpw * (Tc,i - Tc,o) / Cmin * (Tc,i - Th) | [6 empty] | E = Cw * Cpw * (Tc,i - Tc,o) / Cmin * (Tc,i - Th)
Cmin = Cw * Cpw as Cref = infinite | [6 empty] | Cmin = Cw * Cpw as Cref = infinite
ε = (Tc,o - Tc,i) / (Th- Tc,i ) | 90% | [5 empty] | ε = (Tc,o - Tc,i) / (Th- Tc,i ) | 90%
Evaporator | [6 empty] | Evaporator
Qhot = mh * Ch * dT | -0.082546 | kJ/s |  |  |  |  | Qhot = mh * Ch * dT | -0.082546 | kJ/s
Qcold | 0.082546 | kJ/s |  |  |  |  | Qcold | 0.082546 | kJ/s
Simplified | [6 empty] | Simplified
E = Qa / Qmax | [6 empty] | E = Qa / Qmax
E = Cw * Cpw * (Th,o - Th,i) / Cmin * (Th,o - Tc) | [6 empty] | E = Cw * Cpw * (Th,o - Th,i) / Cmin * (Th,o - Tc)
Cmin = Cw * Cpw as Cref = infinite | [6 empty] | Cmin = Cw * Cpw as Cref = infinite
Thus, e = (Th,i - Th,o) / (Th,i - Tc) | 90% | [5 empty] | Thus, e = (Th,i - Th,o) / (Th,i - Tc) | 90%
Th,i = Thot in | 22.2614 | C |  |  |  |  | Th,i = Thot in | 22.2614 | C
Th,o = Thot, out | 16.8614 | C |  |  |  |  | Th,o = Thot, out | 16.8614 | C
Tc,i = Tc, o = T3 | 16.2614 | C |  |  |  |  | Tc,i = Tc, o = T3 | 16.2614 | C
TD = Th,i - Tc | 6 | C |  |  |  |  | TD = Th,i - Tc | 6 | C
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K) |  |  | Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 24.3839 | 6.5429 | 233.76 |  |  |  | 1 - Saturated liquid (100%): subcooling | 33.8284 | 8.5956 | 247.4
2 - liquid + vapour | 16.2614 | 5.0957 | 233.76 |  |  |  | 2 - liquid + vapour | 16.2614 | 5.0957 | 247.4
3 - Saturated vapour (100%): superheat | 16.2614 | 5.0957 | 407.98 | 1.7203 |  |  | 3 - Saturated vapour (100%): superheat | 16.2614 | 5.0957 | 407.98 | 1.7203
4 -liquid + vapour: highly superheated | 25.024 | 6.5429 | 413.024 | 1.7203 |  |  | 4 -liquid + vapour: highly superheated | 35.5714 | 8.5956 | 418.7823 | 1.7203
[7 empty] | 4 calculated with P-bar 850 | 35.1412 |  | 418.5496
[7 empty] | 4 calculated with P-base 900 | 37.3923 |  | 419.7668
[7 empty] | percentage | 0.19112
Isentropic efficiency | [6 empty] | Isentropic efficiency
E | 0.7 | [5 empty] | E | 0.7
E = (h4 - h3) / (h4' - h3) | [6 empty] | E = (h4 - h3) / (h4' - h3)
h4' | 415.1856 | kJ/kg |  |  |  |  | h4' | 423.4118 | kJ/kg
Qcold = Qev | [6 empty] | Qcold = Qev
Qcold = m * (h3-h2) | -0.082546 | kJ/s | sensible and latent heat |  |  |  | Qcold = m * (h3-h2) | -0.082546 | kJ/s | sensible and latent heat
ṁr = flow rate refrigerant | -0.00047381 | kg/s |  |  |  |  | ṁr = flow rate refrigerant | -0.00051405 | kg/s
ṁ water through evaporator | 0.0036535 | kg/s |  |  |  |  | ṁ water through evaporator | 0.0036535 | kg/s
Qhot = Qcon | [6 empty] | Qhot = Qcon
Q = mw * Cpw * dT | 85.9604 | J/s |  |  |  |  | Q = mw * Cpw * dT | 90.4791 | J/s
mw = mf | 0.0059457 | kg/s |  |  |  |  | mw = mf | 0.0018088 | kg/s
Qhot = mr * (h1-h4') | 0.08596 | kJ/s |  |  |  |  | Qhot = mr * (h1-h4') | 0.090479 | kJ/s
ṁr = flow rate refrigerant | -0.00047381 | kg/s |  |  |  |  | ṁr = flow rate refrigerant | -0.00051405 | kg/s
COP cooling | [6 empty] | COP cooling
COPhp = (h4'-h1)/(h4'-h3) | 25.1783 | [5 empty] | COPhp = (h4'-h1)/(h4'-h3) | 11.4058
Win = Qcon / COPhp | 0.0034141 | kJ/s |  |  |  |  | Win = Qcon / COPhp | 0.0079327 | kJ/s
Win = m *dh | 0.0034141 | kJ/s |  |  |  |  | Win = m *dh | 0.0079327 | kJ/s
COPref = (h3-h2) / (h4' - h3) | 24.1783 | [5 empty] | COPref = (h3-h2) / (h4' - h3) | 10.4058
Win = Qev / COPref | 0.0034141 | kJ/s |  |  |  |  | Win = Qev / COPref | 0.0079327 | kJ/s
Total energy use VF | [6 empty] | Total energy use VF
Energy use pumps | [6 empty] | Energy use pumps
| unit | Pump HE1-Ev | Pump HE2 - con | Total |  |  |  | unit | Pump HE1-Ev | Pump HE2 - con | Total
Head | m | 1 | 1 |  |  |  | Head | m | 1 | 1
dP (average pressure difference) | bar | 0.098 | 0.098 |  |  |  | dP (average pressure difference) | bar | 0.098 | 0.098
flow rate | kg/s | 0.0036535 | 0.0026984 |  |  |  | flow rate | kg/s | 0.0036535 | 0.0026984
Capacity | m3/s | 3.6645e-06 | 2.7065e-06 |  |  |  | Capacity | m3/s | 3.6645e-06 | 2.7065e-06
Capacity | m3/h | 0.013192 | 0.0097434 |  |  |  | Capacity | m3/h | 0.013192 | 0.0097434
n pump | % | 72% | 72% |  |  |  | n pump | % | 72% | 72%
Epump | W | 0.049878 | 0.036838 | 0.086717 |  |  | Epump | W | 0.049878 | 0.036838 | 0.086717
Epump | kWh m-2 d-1 | 0.00039903 | 0.00029471 | 0.00069373 |  |  | Epump | kWh m-2 d-1 | 0.00039903 | 0.00029471 | 0.00069373
p water | 997 | kg/m3 |  |  |  |  | p water | 997 | kg/m3
h active | 8 | hrs/yr |  |  |  |  | h active | 8 | hrs/yr
Energy use fans | [6 empty] | Energy use fans
| unit | Indoor fan VF | [5 empty] | unit | Indoor fan VF
Air density | kg/m3 | 1.225 |  |  |  |  | Air density | kg/m3 | 1.225
Uair ducts (not farm) | m/s max | 8 |  |  |  |  | Uair ducts (not farm) | m/s max | 8
Friction loss | Pa | 256.8 |  |  |  |  | Friction loss | Pa | 256.8
Pressure difference | Pa | 296 |  |  |  |  | Pressure difference | Pa | 296
Vair | kg/s | 0.011234 |  |  |  |  | Vair | kg/s | 0.011234
Vair | m3/s | 0.0091705 |  |  |  |  | Vair | m3/s | 0.0091705
Vair | m3/h | 33.0138 |  |  |  |  | Vair | m3/h | 33.0138
n fan | % | 65% | Graamans et al., 2020 |  |  |  | n fan | % | 65% | Graamans et al., 2020
E fan | kW | 0.0041761 |  |  |  |  | E fan | kW | 0.0041761
E fan | kWh d-1 | 0.033409 |  |  |  |  | E fan | kWh d-1 | 0.033409
velocity | m/s | 8 |  |  |  |  | velocity | m/s | 8
p air | 1.225 | kg/m3 |  |  |  |  | p air | 1.225 | kg/m3
Total energy use dark period (winter) | [6 empty] | Total energy use dark period (winter)
Etotal | J m-2 s-1 | J s-1 | kWh m-2 m-1 | kWh m-1 decentralised |  |  | Etotal | J m-2 s-1 | J s-1 | kWh m-2 m-1 | kWh m-1 decentralised
E HP | 3.4141 | 131600.6166 | 0.027313 | 1052.8049 |  |  | E HP | 7.9327 | 305779.5861 | 0.063462 | 2446.2367
Epump | 0.086717 | 3342.6258 | 0.00069373 | 26.741 |  |  | Epump | 0.086717 | 3342.6258 | 0.00069373 | 26.741
Efans | 4.1761 | 160974.1492 | 0.033409 | 1287.7932 |  |  | Efans | 4.1761 | 160974.1492 | 0.033409 | 1287.7932
ELED | 0 | 0 | 0 | 0 |  |  | ELED | 0 | 0 | 0 | 0
Etot | 7.6769 | 295917.3916 | 0.061415 | 2367.3391 |  |  | Etot | 12.1956 | 470096.3611 | 0.097564 | 3760.7709
Total energy use winter | [6 empty] | Total energy use winter
Etotal | J m-2 s-1 | J s-1 | kWh m-2 d-1 | kWh d-1 decentralised |  |  | Etotal | J m-2 s-1 | J s-1 | kWh m-2 d-1 | kWh d-1 decentralised
E HP | 7.813 | 301163.537 | 0.097695 | 3765.8117 |  |  | E HP | 17.9471 | 691800.0056 | 0.22369 | 8622.5634
Epump | 0.187 | 7208.0904 | 0.0022982 | 88.5884 |  |  | Epump | 0.187 | 7208.0904 | 0.0022982 | 88.5884
Efans | 8.3522 | 321948.2983 | 0.10023 | 3863.3796 |  |  | Efans | 8.3522 | 321948.2983 | 0.10023 | 3863.3796
ELED | 57.1429 | 2202658.4092 | 0.91429 | 35242.5345 |  |  | ELED | 57.1429 | 2202658.4092 | 0.91429 | 35242.5345
Etot | 73.495 | 2832978.3349 | 1.1145 | 42960.3142 |  |  | Etot | 83.6292 | 3223614.8035 | 1.2405 | 47817.066 | 47817.066

## Dec_year
Decentralised configuration
LT DHN
Temperatures LT DHN
ATES | Hot source | Cold source
Winter | 24 | 7 | C
Summer | 24 | 7 | C
DHN | uLT | cooling
Winter | 19.75 | 2.75 | C
Summer | 28.25 | 11.25 | C
Temperatures VF
VF (HE3) | Th,i | Th,o | Tc,i | Tc,o
Winter | 24 | 7 | 2.75 | 19.75 | C
Summer | 32.5 | 15.5 | 11.25 | 28.25 | C
neighbourhood connections
Heating demands
Temperature DHN
LT DHN (cold pipe) | HE5, Th,o
MT DHN (warm pipe) | HE5, Th,i
energy losses MT DHN | 15% |  | Loss is expressed as a percentage of total supply. For modern district heating networks a loss of 15-20% is common.
Total heat demand neighbourhood
Tfl, DHW | 328.15 | K | 55C DHW
Tfl, space heat | 343.15 | K | MT Radiator 70C
Tfl return DHW | 285.15 | K | use of tapwater fresh from network (12C)
Tfl space heat return | 323.15 | K | 50C return
εcondener/evaporator | 90%
Monthly | Heat demands | DHW demands | Total demands | % heat | % DHW | Tfl supply (average) | Tfl return (average) | T1 | Qcon | Qcon | HE5 Th,i | HE5 Th,o | T3 | Qev | Qev | COP | Win | Win
| kWh | kWh | kWh |  |  | C | C | C | kWh | kJ/s | C | C | C | kWh | kJ/s | - | kWh | kJ/s
jan | 4670686.5279 | 909161.8651 | 5579848.393 | 83.71% | 16.29% | 67.556 | 43.8084 | 70.1946 | 5579848.393 | 7499.7962 | 19.75 | 2.75 | 0.86111 | 3461095.833 | 4652.0105 | 2.6336 | 2118752.56 | 2847.7857
feb | 4008093.4124 | 909161.8651 | 4917255.2775 | 81.51% | 18.49% | 67.2266 | 42.9741 | 69.9213 | 4917255.2775 | 7317.3442 | 19.75 | 2.75 | 0.86111 | 3050099.3131 | 4538.8383 | 2.6336 | 1867155.9644 | 2778.5059
mrt | 2621144.62 | 909161.8651 | 3530306.4851 | 74.25% | 25.75% | 66.137 | 40.2138 | 69.0174 | 3530306.4851 | 4745.0356 | 19.75 | 2.75 | 0.86111 | 2189795.8876 | 2943.274 | 2.6336 | 1340510.5974 | 1801.7616
apr | 1352536.9487 | 909161.8651 | 2261698.8138 | 59.8% | 40.2% | 63.9703 | 34.7247 | 67.2198 | 2261698.8138 | 3141.2484 | 28.25 | 11.25 | 9.3611 | 1561931.39 | 2169.3492 | 3.2321 | 699767.4238 | 971.8992
may | 0 | 926144.9381 | 926144.9381 | 0% | 100% | 55 | 12 | 59.7778 | 926144.9381 | 1244.8185 | 28.25 | 11.25 | 9.3611 | 681666.9611 | 916.219 | 3.7883 | 244477.9769 | 328.5994
june | 0 | 890189.5028 | 890189.5028 | 0% | 100% | 55 | 12 | 59.7778 | 890189.5028 | 1236.3743 | 28.25 | 11.25 | 9.3611 | 655202.8179 | 910.0039 | 3.7883 | 234986.6849 | 326.3704
july | 0 | 919613.0428 | 919613.0428 | 0% | 100% | 55 | 12 | 59.7778 | 919613.0428 | 1236.039 | 28.25 | 11.25 | 9.3611 | 676859.3149 | 909.7571 | 3.7883 | 242753.7279 | 326.2819
aug | 0 | 919900.8622 | 919900.8622 | 0% | 100% | 55 | 12 | 59.7778 | 919900.8622 | 1236.4259 | 28.25 | 11.25 | 9.3611 | 677071.1576 | 910.0419 | 3.7883 | 242829.7046 | 326.384
sept | 0 | 889960.9796 | 889960.9796 | 0% | 100% | 55 | 12 | 59.7778 | 889960.9796 | 1236.0569 | 28.25 | 11.25 | 9.3611 | 655034.6188 | 909.7703 | 3.7883 | 234926.3607 | 326.2866
oct | 1308164.497 | 909161.8651 | 2217326.3621 | 59% | 41% | 63.8496 | 34.419 | 67.1197 | 2217326.3621 | 2980.2774 | 28.25 | 11.25 | 9.3611 | 1531287.7319 | 2058.1824 | 3.2321 | 686038.6302 | 922.0949
nov | 1914528.3456 | 909161.8651 | 2823690.2107 | 67.8% | 32.2% | 65.1704 | 37.7649 | 68.2154 | 2823690.2107 | 3921.792 | 19.75 | 2.75 | 0.86111 | 1751492.466 | 2432.6284 | 2.6336 | 1072197.7447 | 1489.1635
dec | 3427213.4554 | 909161.8651 | 4336375.3205 | 79.03% | 20.97% | 66.8551 | 42.0329 | 69.6131 | 4336375.3205 | 5828.4615 | 19.75 | 2.75 | 0.86111 | 2689788.2335 | 3615.3068 | 2.6336 | 1646587.087 | 2213.1547
TOTAL YEAR | 19302367.807 | 10909942.381 | 30212310.188 | 63.89% | 36.11% |  |  |  | 30212310.188 |  |  |  |  | 19581325.7253 |  | 2.8419 | 10630984.4627
COP winter | [6 empty] | COP summer | [5 empty] | COP april+oct
assumed about the same | [6 empty] | assumed about the same | [5 empty] | assumed about the same
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K) |  |  | Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K) |  | Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 70.1946 | 21.2689 | 305.14 |  |  |  | 1 | 59.7778 | 16.7488 | 287.58 |  |  | 1 | 67.2198 | 19.8801 | 299.94
2 - liquid + vapour | 0.86111 | 3.0262 | 305.14 |  |  |  | 2 | 9.3611 | 4.0671 | 287.58 |  |  | 2 | 9.3611 | 4.0671 | 299.94
3 - Saturated vapour (100%): superheat | 0.86111 | 3.0262 | 399.34 | 1.7273 |  |  | 3 | 9.3611 | 4.0671 | 404.2 | 1.7231 |  | 3 | 9.3611 | 4.0671 | 404.2 | 1.7231
4 -liquid + vapour: highly superheated | 77.3029 | 21.2689 | 439.706 | 1.7273 |  |  | 4 | 64.678 | 16.7488 | 433.4778 | 1.7231 |  | 4 | 72.9227 | 19.8801 | 436.897 | 1.7231
4 calculated with P-bar 2000 | 74.2698 |  | 438.4777 |  |  |  | 4 calculated with P-bar 1600 | 62.5767 |  | 432.5467 |  |  | 4 calculated with P-bar 1900 | 70.6839 |  | 436.0028
4 calculated with P-base 2400 | 79.0505 |  | 440.4137 |  |  |  | 4 calculated with P-bar 1700 | 65.383 |  | 433.7902 |  |  | 4 calculated with P-bar 2000 | 73.2277 |  | 437.0188
percentage | 0.63444 | [5 empty] | percentage | 0.74878 |  |  |  |  | percentage | 0.88008
Isentropic efficiency | [6 empty] | Isentropic efficiency | [5 empty] | Isentropic efficiency
E | 0.7 | [5 empty] | E | 0.7 |  |  |  |  | E | 0.7
E = (h4 - h3) / (h4' - h3) | [6 empty] | E = (h4 - h3) / (h4' - h3) | [5 empty] | E = (h4 - h3) / (h4' - h3)
h4' | 457.0057 | kJ/kg |  |  |  |  | h4' | 446.0254 | kJ/kg |  |  |  | h4' | 450.91 | kJ/kg
COPhp = (h4'-h1)/(h4'-h3) | 2.6336 | [5 empty] | COPhp = (h4'-h1)/(h4'-h3) | 3.7883 |  |  |  |  | COPhp = (h4'-h1)/(h4'-h3) | 3.2321
uLT + cooling grid temperatures (HP3 +HE6a-...)
Cooling demands from datset 'A Energy pattern neighbourhood'
Product cooling supply temp | 268.15 | K
Floor cooling supply temp | 285.15 | K
Return product cooling | 273.15 | K
Return floor cooling | 295.15 | K
HP4 - active cooling of supermarket product cooling
Efficiency condenser/evaporator | 90%
Monthly | Cooling demands total | Qev HP4 (Superm.) | Qev HP4 (Superm.) | product cooling | space cooling | Th,o ev | Th,i ev | T3 = Tev | Tc,o condenser | Tc,i condenser | T1 = Tcon | Qcon HP4 | Qcon HP4 | COPh | Win | Win | Qev HP4 (Superm.)
| kWh | kWh | kJ/s | % | % | C | C | C | C | C | C | kWh | kJ/s | - | kWh | kJ/s | kg/s
jan | 147608.0666 | 147608.0666 | 198.3979 | 100% | 0% | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 173565.0865 | 233.2864 | 6.6866 | 25957.0199 | 34.8885 | 2.4402
feb | 147608.0666 | 147608.0666 | 198.3979 | 100% | 0% | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 173565.0865 | 258.2814 | 6.6866 | 25957.0199 | 38.6265 | 2.4402
mrt | 147608.0666 | 147608.0666 | 198.3979 | 100% | 0% | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 173565.0865 | 233.2864 | 6.6866 | 25957.0199 | 34.8885 | 2.4402
apr | 150619.8609 | 147608.0666 | 198.3979 | 98% | 2% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 181096.7006 | 251.5232 | 5.4077 | 33488.634 | 46.512 | 2.5461
may | 286552.176 | 147608.0666 | 198.3979 | 51.51% | 48.49% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 181096.7006 | 243.4095 | 5.4077 | 33488.634 | 45.0116 | 2.5461
june | 592952.0472 | 147608.0666 | 198.3979 | 24.89% | 75.11% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 181096.7006 | 251.5232 | 5.4077 | 33488.634 | 46.512 | 2.5461
july | 1012796.1697 | 147608.0666 | 198.3979 | 14.57% | 85.43% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 181096.7006 | 243.4095 | 5.4077 | 33488.634 | 45.0116 | 2.5461
aug | 872647.3426 | 147608.0666 | 198.3979 | 16.91% | 83.09% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 181096.7006 | 243.4095 | 5.4077 | 33488.634 | 45.0116 | 2.5461
sept | 275308.144 | 147608.0666 | 198.3979 | 53.62% | 46.38% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 181096.7006 | 251.5232 | 5.4077 | 33488.634 | 46.512 | 2.5461
oct | 154234.014 | 147608.0666 | 198.3979 | 95.7% | 4.296% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 181096.7006 | 243.4095 | 5.4077 | 33488.634 | 45.0116 | 2.5461
nov | 147608.0666 | 147608.0666 | 198.3979 | 100% | 0% | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 173565.0865 | 241.0626 | 6.6866 | 25957.0199 | 36.0514 | 2.4402
dec | 147608.0666 | 147608.0666 | 198.3979 | 100% | 0% | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 173565.0865 | 233.2864 | 6.6866 | 25957.0199 | 34.8885 | 2.4402
TOTAL YEAR | 4083150.0871 | 1771296.7989 |  | 50% | 50% | [6 empty] | 2135502.3366 |  |  | 364205.5377
COP winter months | [6 empty] | COP summer months
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K) |  |  | Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 21.6389 | 6.0116 | 229.8 |  |  |  | 1 - Saturated liquid (100%): subcooling | 30.1389 | 7.7326 | 241.95
2 - liquid + vapour | -5.5556 | 2.3795 | 229.8 |  |  |  | 2 - liquid + vapour | -5.5556 | 2.3795 | 241.95
3 - Saturated vapour (100%): superheat | -5.5556 | 2.3795 | 395.54 | 1.7312 |  |  | 3 - Saturated vapour (100%): superheat | -5.5556 | 2.3795 | 395.54 | 1.7312
4 -liquid + vapour: highly superheated | 26.7697 | 6.0116 | 415.9419 | 1.7312 |  |  | 4 -liquid + vapour: highly superheated | 34.7022 | 7.7326 | 419.9321 | 1.7312
4 calculated with P-bar 600 | 26.765 |  | 415.965 |  |  |  | 4 calculated with P-bar 750 | 33.568 |  | 419.3108
4 calculated with P-bar 625 | 26.8667 |  | 415.4667 |  |  |  | 4 calculated with P-bar 800 | 36.006 |  | 420.6462
percentage | 0.04632 | [5 empty] | percentage | 0.46522
Isentropic efficiency | [6 empty] | Isentropic efficiency
E | 0.7 | [5 empty] | E | 0.7
E = (h4 - h3) / (h4' - h3) | [6 empty] | E = (h4 - h3) / (h4' - h3)
h4' | 424.6855 | kJ/kg |  |  |  |  | h4' | 430.3858 | kJ/kg
COPhp = (h4'-h1)/(h4'-h3) | 6.6866 | [5 empty] | COPhp = (h4'-h1)/(h4'-h3) | 5.4077
Cpw | 4184 | J/kg K |  |  |  |  | Cpw | 4184 | J/kg K
HE5a-.. passive cooling (floor cooling)
COP summer months
Monthly | Cooling demands total | Qev HP5a-.. | Qev HP5 | product cooling | space cooling | Th,i | Th,o | T3 | Tc,i | Tc,o | T1 | Qcon | Qcon | COP | Win | Win |  | Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
| kWh | kWh | kJ/s | % | % | C | C | C | C | C | C | kWh | kJ/s |  | kWh | kJ/s |  | 1 | 30.1389 | 7.7326 | 241.95
jan | 147608.0666 | 0 | 0 | 100% | 0% | [12 empty] | 2 | 10.8889 | 4.2757 | 241.95
feb | 147608.0666 | 0 | 0 | 100% | 0% | [12 empty] | 3 | 10.8889 | 4.2757 | 405.04 | 1.7228
mrt | 147608.0666 | 0 | 0 | 100% | 0% | [12 empty] | 4 | 32.2299 | 7.7326 | 417.3609 | 1.7228
apr | 150619.8609 | 3011.7943 | 4.0481 | 98% | 2% | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 3336.838 | 4.485 | 10.2658 | 325.0437 | 0.43689 |  | 4 calculated with P-bar 750 | 31.1095 |  | 416.7538
may | 286552.176 | 138944.1094 | 186.7528 | 51.51% | 48.49% | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 153939.4582 | 206.9079 | 10.2658 | 14995.3488 | 20.155 |  | 4 calculated with P-bar 800 | 33.518 |  | 418.0587
june | 592952.0472 | 445343.9807 | 598.5806 | 24.89% | 75.11% | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 493407.1072 | 663.1816 | 10.2658 | 48063.1265 | 64.601 |  | percentage | 0.46522
july | 1012796.1697 | 865188.1031 | 1162.8872 | 14.57% | 85.43% | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 958562.3196 | 1288.3902 | 10.2658 | 93374.2165 | 125.503
aug | 872647.3426 | 725039.276 | 974.5152 | 16.91% | 83.09% | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 803288.1263 | 1079.6883 | 10.2658 | 78248.8503 | 105.1732 |  | Isentropic efficiency
sept | 275308.144 | 127700.0774 | 171.6399 | 53.62% | 46.38% | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 141481.9297 | 190.1639 | 10.2658 | 13781.8523 | 18.524 |  | E | 0.7
oct | 154234.014 | 6625.9474 | 8.9058 | 95.7% | 4.296% | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 7341.0435 | 9.867 | 10.2658 | 715.0961 | 0.96115 |  | E = (h4 - h3) / (h4' - h3)
nov | 147608.0666 | 0 | 0 | 100% | 0% | [12 empty] | h4' | 422.6413 | kJ/kg
dec | 147608.0666 | 0 | 0 | 100% | 0% | [12 empty] | COPhp = (h4'-h1)/(h4'-h3) | 10.2658
TOTAL YEAR | 4083150.0871 | 2311853.2882 |  | 50% | 50% | [6 empty] | 2561356.8225
Sizing VF + ATES
VF
Year-round balance
Qhe3 + QHP5 + QHP4 = QHP3 + Qlosses
QHP5 con | 2561356.8225 | kWh y-1
QHP4 con | 2135502.3366 | kWh y-1
QHP3 ev | 19581325.7253 | kWh y-1
Qlosses | 2937198.8588 | kWh y-1
QHe3 | 17821665.425 | kWh y-1
QHE3 per m2 cultivation total | 462.3417 | kWh m-2 y-1
m2 cultivation | 38546.5222 | m2
Monthly | Qheat VF (Qhe3) | Qheat VF (Qhe3) | m flow Qhe3 | Qcon HP4 + Qcon HP5 (NBH cooling) | Qcon HP4 + Qcon HP5 (NBH cooling) | Qlosses uLT | Qlosses uLT | Qev (HP3) | Qev (HP3) | m flow ev HP2 | QHE4 (ATES) | QHE4 (ATES) | m ATES
| kWh | kJ/s | kg/s | kWh | kJ/s | kWh | kJ/s | kWh | kJ/s | kg/s | kWh | kJ/s | kg/s
jan | 1425347.7729 | 1915.79 | 26.9344 | 173565.0865 | 233.2864 | 519164.3749 | 697.8016 | 3461095.833 | 4652.0105 | 65.4034 | 2381347.3485 | 3200.7357 | 33.4797
feb | 1287410.8917 | 1915.79 | 26.9344 | 173565.0865 | 258.2814 | 457514.897 | 680.8257 | 3050099.3131 | 4538.8383 | 63.8123 | 2046638.2319 | 3045.5926 | 28.774
mrt | 1425347.7729 | 1915.79 | 26.9344 | 173565.0865 | 233.2864 | 328469.3831 | 441.4911 | 2189795.8876 | 2943.274 | 41.38 | 919352.4114 | 1235.6887 | 12.9253
apr | 1525071.3648 | 2118.1547 | 29.7795 | 184433.5386 | 256.0082 | 234289.7085 | 325.4024 | 1561931.39 | 2169.3492 | 30.4992 | 86716.1952 | 120.5887 | -1.2192
may | 1575907.0769 | 2118.1547 | 29.7795 | 335036.1587 | 450.3174 | 102250.0442 | 137.4329 | 681666.9611 | 916.219 | 12.8813 | -1127026.2304 | -1514.8202 | 15.845
june | 1525071.3648 | 2118.1547 | 29.7795 | 674503.8078 | 914.7048 | 98280.4227 | 136.5006 | 655202.8179 | 910.0039 | 12.7939 | -1446091.9319 | -1986.355 | 20.3308
july | 1575907.0769 | 2118.1547 | 29.7795 | 1139659.0202 | 1531.7998 | 101528.8972 | 136.4636 | 676859.3149 | 909.7571 | 12.7904 | -1937177.885 | -2603.7337 | 27.2351
aug | 1575907.0769 | 2118.1547 | 29.7795 | 984384.8269 | 1323.0979 | 101560.6736 | 136.5063 | 677071.1576 | 910.0419 | 12.7944 | -1781660.0726 | -2394.7044 | 25.0486
sept | 1525071.3648 | 2118.1547 | 29.7795 | 322578.6303 | 441.6871 | 98255.1928 | 136.4655 | 655034.6188 | 909.7703 | 12.7906 | -1094360.1835 | -1513.6059 | 15.3858
oct | 1575907.0769 | 2118.1547 | 29.7795 | 188437.7441 | 253.2765 | 229693.1598 | 308.7274 | 1531287.7319 | 2058.1824 | 28.9363 | -3363.9294 | -4.5214 | 0.047294
nov | 1379368.8125 | 1915.79 | 26.9344 | 173565.0865 | 241.0626 | 262723.8699 | 364.8943 | 1751492.466 | 2432.6284 | 34.2007 | 461282.4369 | 640.6701 | 6.4852
dec | 1425347.7729 | 1915.79 | 26.9344 | 173565.0865 | 233.2864 | 403468.235 | 542.296 | 2689788.2335 | 3615.3068 | 50.8282 | 1494343.6091 | 2008.5264 | 21.0092
TOTAL YEAR | 17821665.425 |  |  | 4696859.1591 |  | 2937198.8588 |  | 19581325.7253 |  |  | 0 |  |  | - | -
TOTAL ENERGY USE
Vertical farm
| kWh m-2 y-1 | kWh y-1
Energy use fans | 36.5826 | 1410133.5467
Energy use pumps | 0.83885 | 32334.7803
HP1 | 62.6222 | 2413866.1283
LEDs | 333.7143 | 12863525.1098
Total energy use VF |  | 16719859.5651 | equally divided over the year
16719.8596
Pumps
Epump (kW) = (dp * Capacity)/ 36 * n
P = 0.981 * head * SG
SG specific gravity fluid, for water | 1
p water | 997 | kg/m3
Assumptions
Efficiency | 72% | Kaya et al., 2021
Head HE3-HE4- ev HP2 | 1 | m
Head ATES | 200 | m
Pumps DHN
Pump energy DHN | 0,2 * V [m3/y] | KoWaNet (p. 84)
Q = m * Cp * dT
LT Grid
Month | Q | Q | m | m | Pumps LT DHN
| kWh | MJ/y | kg / month | m3/month | kWh
jan | 3980260.2079 | 14328936.7484 | 201452827.9781 | 202059.005 | 40411.801
feb | 3507614.21 | 12627411.1561 | 177530805.816 | 178065.0008 | 35613.0002
mrt | 2518265.2708 | 9065754.9748 | 127456908.3174 | 127840.4296 | 25568.0859
apr | 1796221.0985 | 6466395.9547 | 90912101.4882 | 91185.6585 | 18237.1317
may | 783917.0053 | 2822101.2191 | 39676375.2543 | 39795.7625 | 7959.1525
june | 753483.2406 | 2712539.6663 | 38136031.7497 | 38250.7841 | 7650.1568
july | 778388.2122 | 2802197.5638 | 39396546.5606 | 39515.0918 | 7903.0184
aug | 778631.8312 | 2803074.5923 | 39408876.8461 | 39527.4592 | 7905.4918
sept | 753289.8116 | 2711843.3219 | 38126241.7314 | 38240.9646 | 7648.1929
oct | 1760980.8916 | 6339531.2099 | 89128489.6233 | 89396.6797 | 17879.3359
nov | 2014216.3359 | 7251178.8092 | 101945489.9502 | 102252.2467 | 20450.4493
dec | 3093256.4685 | 11135723.2865 | 156558925.9717 | 157030.016 | 31406.0032
Total year | 22518524.5841 | 81066688.5029
Total monthly
Month | VF fans, pumps | VF HP1 | VF LED | ATES pump | Pumps DHN | Building heating (HP3) | NBH cooling (HP4) | User-related electricity | EV charging | Total electricity
| MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh
jan | 120.2057 | 201.1555 | 1071.9604 | 68.0811 | 40.4118 | 2118.7526 | 25.957 | 1053.7724 | 22.6975 | 4722.994
feb | 120.2057 | 201.1555 | 1071.9604 | 58.512 | 35.613 | 1867.156 | 25.957 | 912.9277 | 22.6975 | 4316.1847
mrt | 120.2057 | 201.1555 | 1071.9604 | 26.2837 | 25.5681 | 1340.5106 | 25.957 | 949.9959 | 22.6975 | 3784.3343
apr | 120.2057 | 201.1555 | 1071.9604 | -2.4792 | 18.2371 | 699.7674 | 33.8137 | 850.0233 | 22.6975 | 3015.3815
may | 120.2057 | 201.1555 | 1071.9604 | 32.2209 | 7.9592 | 244.478 | 48.484 | 840.6567 | 22.6975 | 2589.8178
june | 120.2057 | 201.1555 | 1071.9604 | 41.3428 | 7.6502 | 234.9867 | 81.5518 | 807.8451 | 22.6975 | 2589.3955
july | 120.2057 | 201.1555 | 1071.9604 | 55.3826 | 7.903 | 242.7537 | 126.8629 | 815.9337 | 22.6975 | 2664.8549
aug | 120.2057 | 201.1555 | 1071.9604 | 50.9364 | 7.9055 | 242.8297 | 111.7375 | 830.2678 | 22.6975 | 2659.696
sept | 120.2057 | 201.1555 | 1071.9604 | 31.287 | 7.6482 | 234.9264 | 47.2705 | 814.1013 | 22.6975 | 2551.2524
oct | 120.2057 | 201.1555 | 1071.9604 | 0.096172 | 17.8793 | 686.0386 | 34.2037 | 916.5946 | 22.6975 | 3070.8315
nov | 120.2057 | 201.1555 | 1071.9604 | 13.1877 | 20.4504 | 1072.1977 | 25.957 | 963.9632 | 22.6975 | 3511.7753
dec | 120.2057 | 201.1555 | 1071.9604 | 42.7223 | 31.406 | 1646.5871 | 25.957 | 1063.0444 | 22.6975 | 4225.7358
TOTAL YEAR | 1442.4683 | 2413.8661 | 12863.5251 | 417.5734 | 228.6318 | 10630.9845 | 613.7091 | 10819.1261 | 272.3695 | 39702.2539
Heat balance
Month | Heat demand | Losses grid | VF produce (QHE3) | ATES extracted/stored | HP3 Win | NBH cooling (Qcon HP3+5) | Total supply | total demand
| MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh
jan | 5579.8484 | 519.1644 | 1425.3478 | 2381.3473 | 2118.7526 | 173.5651 | 6099.0128 | 6099.0128
feb | 4917.2553 | 457.5149 | 1287.4109 | 2046.6382 | 1867.156 | 173.5651 | 5374.7702 | 5374.7702
mrt | 3530.3065 | 328.4694 | 1425.3478 | 919.3524 | 1340.5106 | 173.5651 | 3858.7759 | 3858.7759
apr | 2261.6988 | 234.2897 | 1525.0714 | 86.7162 | 699.7674 | 184.4335 | 2495.9885 | 2495.9885
may | 926.1449 | 102.25 | 1575.9071 | -1127.0262 | 244.478 | 335.0362 | 1028.395 | 1028.395
june | 890.1895 | 98.2804 | 1525.0714 | -1446.0919 | 234.9867 | 674.5038 | 988.4699 | 988.4699
july | 919.613 | 101.5289 | 1575.9071 | -1937.1779 | 242.7537 | 1139.659 | 1021.1419 | 1021.1419
aug | 919.9009 | 101.5607 | 1575.9071 | -1781.6601 | 242.8297 | 984.3848 | 1021.4615 | 1021.4615
sept | 889.961 | 98.2552 | 1525.0714 | -1094.3602 | 234.9264 | 322.5786 | 988.2162 | 988.2162
oct | 2217.3264 | 229.6932 | 1575.9071 | -3.3639 | 686.0386 | 188.4377 | 2447.0195 | 2447.0195
nov | 2823.6902 | 262.7239 | 1379.3688 | 461.2824 | 1072.1977 | 173.5651 | 3086.4141 | 3086.4141
dec | 4336.3753 | 403.4682 | 1425.3478 | 1494.3436 | 1646.5871 | 173.5651 | 4739.8436 | 4739.8436
TOTAL YEAR | 30212.3102 | 2937.1989 | 17821.6654 | 0 | 10630.9845 | 4696.8592 | 33149.509 | 33149.509
Cold balane
Month | VF demand (QHE3) | NBH cooling (HP3+QHE6a-..) | HP3 cold produced | ATES extracted/stored | Heat gains grid | Total supply | Total demand
| MWh | MWh | MWh | MWh | MWh | MWh | MWh
jan | 1425.3478 | 173.5651 | 3461.0958 | -2381.3473 | 519.1644 | 1598.9129 | 1598.9129
feb | 1287.4109 | 173.5651 | 3050.0993 | -2046.6382 | 457.5149 | 1460.976 | 1460.976
mrt | 1425.3478 | 173.5651 | 2189.7959 | -919.3524 | 328.4694 | 1598.9129 | 1598.9129
apr | 1525.0714 | 184.4335 | 1561.9314 | -86.7162 | 234.2897 | 1709.5049 | 1709.5049
may | 1575.9071 | 335.0362 | 681.667 | 1127.0262 | 102.25 | 1910.9432 | 1910.9432
june | 1525.0714 | 674.5038 | 655.2028 | 1446.0919 | 98.2804 | 2199.5752 | 2199.5752
july | 1575.9071 | 1139.659 | 676.8593 | 1937.1779 | 101.5289 | 2715.5661 | 2715.5661
aug | 1575.9071 | 984.3848 | 677.0712 | 1781.6601 | 101.5607 | 2560.2919 | 2560.2919
sept | 1525.0714 | 322.5786 | 655.0346 | 1094.3602 | 98.2552 | 1847.65 | 1847.65
oct | 1575.9071 | 188.4377 | 1531.2877 | 3.3639 | 229.6932 | 1764.3448 | 1764.3448
nov | 1379.3688 | 173.5651 | 1751.4925 | -461.2824 | 262.7239 | 1552.9339 | 1552.9339
dec | 1425.3478 | 173.5651 | 2689.7882 | -1494.3436 | 403.4682 | 1598.9129 | 1598.9129
TOTAL YEAR | 17821.6654 | 4696.8592 | 19581.3257 | 0 | 2937.1989 | 22518.5246 | 22518.5246

## Dec_daily
Decentralised configuration
WINTER PROFILES | [15 empty] | SUMMER PROFILES
neighbourhood profile with grid concious EV | [15 empty] | neighbourhood profile with grid concious EV
Data from datset 'A. Energy pattern neighbourhood' | [15 empty] | Data from datset 'A. Energy pattern neighbourhood'
Ta | 304.35 | K | [13 empty] | Ta | 304.35 | K
Tfl, DHW | 328.15 | K | [13 empty] | Tfl, DHW | 328.15 | K
Tfl, space heat | 343.15 | K | [13 empty] | Tfl, space heat | 343.15 | K
Tfl return DHW | 285.15 | K | [13 empty] | Tfl return DHW | 285.15 | K
Tfl space heat return | 323.15 | K | [13 empty] | Tfl space heat return | 323.15 | K
Eff cond/evap | 90% | [14 empty] | Eff cond/evap | 90%
water/water HE3; ε | 80%
WINTERDAY | Heat demands | DHW demands | Total demands | % heat | % DHW | Tf (Tc,o) | Tf (Tc,i) | T1 | Qcon | Th,i HE3 | Th,o HE3 | T3 | Qev | COP | Win | Summer day | Heat demands | DHW demands | Total demands | % heat | % DHW | Tf (Tc,o) | Tf (Tc,i) | T1 | Qcon | Th,i HE3 | Th,o HE3 | T3 | Qev | COP | Win
18 January | kW | kW | kW |  |  | C | C | C | kW | C | C | C | kW |  | kW | 24 July | kW | kW | kW |  |  | C | C | C | kW | C | C | C | kW |  | kW
0:00 | 4436.4779 | 558.3164 | 4994.7943 | 88.82% | 11.18% | 68.3233 | 45.7524 | 70.8312 | 4994.7943 | 19.75 | 2.75 | 0.86111 | 3098.1956 | 2.6336 | 1896.5987 | 0:00 | 0 | 558.3164 | 558.3164 | 0% | 100% | 55 | 12 | 59.7778 | 558.3164 | 28.25 | 11.25 | 9.3611 | 410.9355 | 3.7883 | 147.3809
1:00 | 3700.7948 | 452.3828 | 4153.1777 | 89.11% | 10.89% | 68.3661 | 45.8609 | 70.8667 | 4153.1777 | 19.75 | 2.75 | 0.86111 | 2576.1535 | 2.6336 | 1577.0242 | 1:00 | 0 | 452.3828 | 452.3828 | 0% | 100% | 55 | 12 | 59.7778 | 452.3828 | 28.25 | 11.25 | 9.3611 | 332.9656 | 3.7883 | 119.4172
2:00 | 3653.1934 | 455.0478 | 4108.2412 | 88.92% | 11.08% | 68.3385 | 45.7909 | 70.8438 | 4108.2412 | 19.75 | 2.75 | 0.86111 | 2548.2801 | 2.6336 | 1559.9611 | 2:00 | 0 | 455.0478 | 455.0478 | 0% | 100% | 55 | 12 | 59.7778 | 455.0478 | 28.25 | 11.25 | 9.3611 | 334.9271 | 3.7883 | 120.1207
3:00 | 3957.8182 | 463.0428 | 4420.8611 | 89.53% | 10.47% | 68.4289 | 46.0199 | 70.9188 | 4420.8611 | 19.75 | 2.75 | 0.86111 | 2742.1935 | 2.6336 | 1678.6676 | 3:00 | 0 | 463.0428 | 463.0428 | 0% | 100% | 55 | 12 | 59.7778 | 463.0428 | 28.25 | 11.25 | 9.3611 | 340.8117 | 3.7883 | 122.2312
4:00 | 4253.586 | 485.6953 | 4739.2813 | 89.75% | 10.25% | 68.4628 | 46.1056 | 70.9469 | 4739.2813 | 19.75 | 2.75 | 0.86111 | 2939.7047 | 2.6336 | 1799.5766 | 4:00 | 0 | 485.6953 | 485.6953 | 0% | 100% | 55 | 12 | 59.7778 | 485.6953 | 28.25 | 11.25 | 9.3611 | 357.4845 | 3.7883 | 128.2108
5:00 | 4296.5277 | 778.8447 | 5075.3724 | 84.65% | 15.35% | 67.6982 | 44.1687 | 70.3126 | 5075.3724 | 19.75 | 2.75 | 0.86111 | 3148.177 | 2.6336 | 1927.1954 | 5:00 | 0 | 778.8447 | 778.8447 | 0% | 100% | 55 | 12 | 59.7778 | 778.8447 | 28.25 | 11.25 | 9.3611 | 573.2501 | 3.7883 | 205.5946
6:00 | 5650.3317 | 1321.1711 | 6971.5028 | 81.05% | 18.95% | 67.1573 | 42.7986 | 69.8639 | 6971.5028 | 19.75 | 2.75 | 0.86111 | 4324.3181 | 2.6336 | 2647.1847 | 6:00 | 0 | 1321.1711 | 1321.1711 | 0% | 100% | 55 | 12 | 59.7778 | 1321.1711 | 28.25 | 11.25 | 9.3611 | 972.4166 | 3.7883 | 348.7545
7:00 | 9630.278 | 1395.1247 | 11025.4028 | 87.35% | 12.65% | 68.1019 | 45.1916 | 70.6475 | 11025.4028 | 19.75 | 2.75 | 0.86111 | 6838.8911 | 2.6336 | 4186.5117 | 7:00 | 0 | 1395.1247 | 1395.1247 | 0% | 100% | 55 | 12 | 59.7778 | 1395.1247 | 28.25 | 11.25 | 9.3611 | 1026.8484 | 3.7883 | 368.2763
8:00 | 12145.027 | 1495.7283 | 13640.7552 | 89.03% | 10.97% | 68.3552 | 45.8332 | 70.8577 | 13640.7552 | 19.75 | 2.75 | 0.86111 | 8461.1548 | 2.6336 | 5179.6004 | 8:00 | 0 | 1495.7283 | 1495.7283 | 0% | 100% | 55 | 12 | 59.7778 | 1495.7283 | 28.25 | 11.25 | 9.3611 | 1100.8952 | 3.7883 | 394.833
9:00 | 13164.8072 | 1539.7007 | 14704.5079 | 89.53% | 10.47% | 68.4294 | 46.021 | 70.9192 | 14704.5079 | 19.75 | 2.75 | 0.86111 | 9120.9845 | 2.6336 | 5583.5233 | 9:00 | 0 | 1539.7007 | 1539.7007 | 0% | 100% | 55 | 12 | 59.7778 | 1539.7007 | 28.25 | 11.25 | 9.3611 | 1133.2601 | 3.7883 | 406.4406
10:00 | 12404.5562 | 1337.1611 | 13741.7172 | 90.27% | 9.731% | 68.5404 | 46.3023 | 71.0113 | 13741.7172 | 19.75 | 2.75 | 0.86111 | 8523.78 | 2.6336 | 5217.9372 | 10:00 | 0 | 1337.1611 | 1337.1611 | 0% | 100% | 55 | 12 | 59.7778 | 1337.1611 | 28.25 | 11.25 | 9.3611 | 984.1856 | 3.7883 | 352.9755
11:00 | 11151.3131 | 1338.4936 | 12489.8067 | 89.28% | 10.72% | 68.3925 | 45.9277 | 70.8886 | 12489.8067 | 19.75 | 2.75 | 0.86111 | 7747.2388 | 2.6336 | 4742.5679 | 11:00 | 0 | 1338.4936 | 1338.4936 | 0% | 100% | 55 | 12 | 59.7778 | 1338.4936 | 28.25 | 11.25 | 9.3611 | 985.1664 | 3.7883 | 353.3272
12:00 | 10825.6561 | 1374.471 | 12200.1271 | 88.73% | 11.27% | 68.3101 | 45.7189 | 70.8202 | 12200.1271 | 19.75 | 2.75 | 0.86111 | 7567.5549 | 2.6336 | 4632.5722 | 12:00 | 0 | 1374.471 | 1374.471 | 0% | 100% | 55 | 12 | 59.7778 | 1374.471 | 28.25 | 11.25 | 9.3611 | 1011.6467 | 3.7883 | 362.8243
13:00 | 10651.54 | 1201.2463 | 11852.7863 | 89.87% | 10.13% | 68.4798 | 46.1488 | 70.961 | 11852.7863 | 19.75 | 2.75 | 0.86111 | 7352.1047 | 2.6336 | 4500.6817 | 13:00 | 0 | 1201.2463 | 1201.2463 | 0% | 100% | 55 | 12 | 59.7778 | 1201.2463 | 28.25 | 11.25 | 9.3611 | 884.1488 | 3.7883 | 317.0975
14:00 | 10946.3057 | 1050.0079 | 11996.3136 | 91.25% | 8.753% | 68.6871 | 46.674 | 71.133 | 11996.3136 | 19.75 | 2.75 | 0.86111 | 7441.1325 | 2.6336 | 4555.1811 | 14:00 | 0 | 1050.0079 | 1050.0079 | 0% | 100% | 55 | 12 | 59.7778 | 1050.0079 | 28.25 | 11.25 | 9.3611 | 772.8333 | 3.7883 | 277.1746
15:00 | 11212.4321 | 1157.2739 | 12369.706 | 90.64% | 9.356% | 68.5966 | 46.4448 | 71.058 | 12369.706 | 19.75 | 2.75 | 0.86111 | 7672.7422 | 2.6336 | 4696.9639 | 15:00 | 0 | 1157.2739 | 1157.2739 | 0% | 100% | 55 | 12 | 59.7778 | 1157.2739 | 28.25 | 11.25 | 9.3611 | 851.784 | 3.7883 | 305.49
16:00 | 11198.3129 | 1557.0231 | 12755.3361 | 87.79% | 12.21% | 68.169 | 45.3614 | 70.7031 | 12755.3361 | 19.75 | 2.75 | 0.86111 | 7911.9427 | 2.6336 | 4843.3934 | 16:00 | 0 | 1557.0231 | 1557.0231 | 0% | 100% | 55 | 12 | 59.7778 | 1557.0231 | 28.25 | 11.25 | 9.3611 | 1146.0099 | 3.7883 | 411.0133
17:00 | 12538.9332 | 2370.5128 | 14909.4459 | 84.1% | 15.9% | 67.6151 | 43.9582 | 70.2436 | 14909.4459 | 19.75 | 2.75 | 0.86111 | 9248.1045 | 2.6336 | 5661.3414 | 17:00 | 0 | 2370.5128 | 2370.5128 | 0% | 100% | 55 | 12 | 59.7778 | 2370.5128 | 28.25 | 11.25 | 9.3611 | 1744.7596 | 3.7883 | 625.7532
18:00 | 14138.5762 | 2355.189 | 16493.7653 | 85.72% | 14.28% | 67.8581 | 44.5739 | 70.4452 | 16493.7653 | 19.75 | 2.75 | 0.86111 | 10230.8339 | 2.6336 | 6262.9314 | 18:00 | 0 | 2355.189 | 2355.189 | 0% | 100% | 55 | 12 | 59.7778 | 2355.189 | 28.25 | 11.25 | 9.3611 | 1733.4809 | 3.7883 | 621.7081
19:00 | 13087.513 | 1962.7686 | 15050.2816 | 86.96% | 13.04% | 68.0438 | 45.0443 | 70.5993 | 15050.2816 | 19.75 | 2.75 | 0.86111 | 9335.4628 | 2.6336 | 5714.8188 | 19:00 | 0 | 1962.7686 | 1962.7686 | 0% | 100% | 55 | 12 | 59.7778 | 1962.7686 | 28.25 | 11.25 | 9.3611 | 1444.6491 | 3.7883 | 518.1194
20:00 | 12442.0153 | 1672.9504 | 14114.9657 | 88.15% | 11.85% | 68.2222 | 45.4961 | 70.7473 | 14114.9657 | 19.75 | 2.75 | 0.86111 | 8755.3004 | 2.6336 | 5359.6653 | 20:00 | 0 | 1672.9504 | 1672.9504 | 0% | 100% | 55 | 12 | 59.7778 | 1672.9504 | 28.25 | 11.25 | 9.3611 | 1231.3354 | 3.7883 | 441.615
21:00 | 11316.6001 | 1399.7885 | 12716.3885 | 88.99% | 11.01% | 68.3488 | 45.8171 | 70.8524 | 12716.3885 | 19.75 | 2.75 | 0.86111 | 7887.7841 | 2.6336 | 4828.6044 | 21:00 | 0 | 1399.7885 | 1399.7885 | 0% | 100% | 55 | 12 | 59.7778 | 1399.7885 | 28.25 | 11.25 | 9.3611 | 1030.281 | 3.7883 | 369.5074
22:00 | 9055.3774 | 1175.9289 | 10231.3063 | 88.51% | 11.49% | 68.276 | 45.6325 | 70.7919 | 10231.3063 | 19.75 | 2.75 | 0.86111 | 6346.325 | 2.6336 | 3884.9813 | 22:00 | 0 | 1175.9289 | 1175.9289 | 0% | 100% | 55 | 12 | 59.7778 | 1175.9289 | 28.25 | 11.25 | 9.3611 | 865.5145 | 3.7883 | 310.4144
23:00 | 6585.8388 | 813.4896 | 7399.3284 | 89.01% | 10.99% | 68.3509 | 45.8222 | 70.8541 | 7399.3284 | 19.75 | 2.75 | 0.86111 | 4589.6918 | 2.6336 | 2809.6365 | 23:00 | 0 | 813.4896 | 813.4896 | 0% | 100% | 55 | 12 | 59.7778 | 813.4896 | 28.25 | 11.25 | 9.3611 | 598.7497 | 3.7883 | 214.7399
TOTAL DAY | 222443.812 | 29711.3594 | 252155.1714 | 88.22% | 11.78% |  |  |  | 252155.1714 |  |  |  | 156408.0512 |  | 95747.1202 | TOTAL DAY | 0 | 29711.3594 | 29711.3594 | 0% | 100% | 70 | 50 |  | 29711.3594 |  |  |  | 21868.3396 |  | 7843.0197
Data user-related electricity and electric vehicle from datset 'A. Energy pattern neighbourhood' | [15 empty] | Data user-related electricity and electric vehicle from datset 'A. Energy pattern neighbourhood'
Daily profile, winter | [15 empty] | Daily profile, winter
18 January (on average coldest winter weekday) | [15 empty] | 24 July warmest weekday
| URE | EV | HP3a-… | Total | [12 empty] | URE | HP | EV | Total
| kW | kW | kW | kW | [12 empty] | kW | kW | kW | kW
0:00 | 277.3137 | 443.4672 | 1896.5987 | 2617.3796 | [11 empty] | 0:00 | 288.9848 | 147.3809 | 443.4672 | 879.8329
1:00 | 237.5549 | 389.7136 | 1577.0242 | 2204.2927 | [11 empty] | 1:00 | 246.2969 | 119.4172 | 389.7136 | 755.4277
2:00 | 217.0093 | 309.0832 | 1559.9611 | 2086.0536 | [11 empty] | 2:00 | 219.9491 | 120.1207 | 309.0832 | 649.153
3:00 | 206.4166 | 255.3296 | 1678.6676 | 2140.4138 | [11 empty] | 3:00 | 204.6696 | 122.2312 | 255.3296 | 582.2304
4:00 | 200.7646 | 188.1376 | 1799.5766 | 2188.4788 | [11 empty] | 4:00 | 200.8105 | 128.2108 | 188.1376 | 517.159
5:00 | 213.2419 | 134.384 | 1927.1954 | 2274.8214 | [11 empty] | 5:00 | 208.5809 | 205.5946 | 134.384 | 548.5594
6:00 | 253.9743 | 80.6304 | 2647.1847 | 2981.7895 | [11 empty] | 6:00 | 233.9492 | 348.7545 | 80.6304 | 663.3341
7:00 | 322.9072 | 174.6992 | 4186.5117 | 4684.118 | [11 empty] | 7:00 | 283.302 | 368.2763 | 174.6992 | 826.2775
8:00 | 359.4094 | 295.6448 | 5179.6004 | 5834.6546 | [11 empty] | 8:00 | 347.1998 | 394.833 | 295.6448 | 1037.6776
9:00 | 376.9609 | 416.5904 | 5583.5233 | 6377.0747 | [11 empty] | 9:00 | 393.9319 | 406.4406 | 416.5904 | 1216.9629
10:00 | 381.2817 | 349.3984 | 5217.9372 | 5948.6173 | [11 empty] | 10:00 | 402.8935 | 352.9755 | 349.3984 | 1105.2673
11:00 | 370.5403 | 282.2064 | 4742.5679 | 5395.3146 | [11 empty] | 11:00 | 407.6655 | 353.3272 | 282.2064 | 1043.1991
12:00 | 365.423 | 228.4528 | 4632.5722 | 5226.448 | [11 empty] | 12:00 | 415.1209 | 362.8243 | 228.4528 | 1006.398
13:00 | 367.7989 | 255.3296 | 4500.6817 | 5123.8102 | [11 empty] | 13:00 | 404.346 | 317.0975 | 255.3296 | 976.7732
14:00 | 360.3372 | 241.8912 | 4555.1811 | 5157.4095 | [11 empty] | 14:00 | 401.2686 | 277.1746 | 241.8912 | 920.3343
15:00 | 359.8236 | 241.8912 | 4696.9639 | 5298.6787 | [11 empty] | 15:00 | 405.8541 | 305.49 | 241.8912 | 953.2353
16:00 | 365.2218 | 268.768 | 4843.3934 | 5477.3832 | [11 empty] | 16:00 | 450.9235 | 411.0133 | 268.768 | 1130.7048
17:00 | 406.2677 | 144.7212 | 5661.3414 | 6212.3303 | [11 empty] | 17:00 | 542.3265 | 625.7532 | 144.7212 | 1312.8009
18:00 | 522.6252 | 403.152 | 6262.9314 | 7188.7086 | [11 empty] | 18:00 | 542.0794 | 621.7081 | 403.152 | 1566.9395
19:00 | 530.3969 | 524.0976 | 5714.8188 | 6769.3134 | [11 empty] | 19:00 | 505.6715 | 518.1194 | 524.0976 | 1547.8885
20:00 | 502.0107 | 483.7824 | 5359.6653 | 6345.4584 | [11 empty] | 20:00 | 465.7749 | 441.615 | 483.7824 | 1391.1724
21:00 | 461.4897 | 443.4672 | 4828.6044 | 5733.5614 | [11 empty] | 21:00 | 416.2452 | 369.5074 | 443.4672 | 1229.2199
22:00 | 424.7429 | 403.152 | 3884.9813 | 4712.8762 | [11 empty] | 22:00 | 384.2443 | 310.4144 | 403.152 | 1097.8107
23:00 | 379.8485 | 430.0288 | 2809.6365 | 3619.5139 | [11 empty] | 23:00 | 340.0549 | 214.7399 | 430.0288 | 984.8236
Neighbourhood cooling | [15 empty] | Neighbourhood cooling
Data cooling demand from datset 'A. Energy pattern neighbourhood' | [15 empty] | Data cooling demand from datset 'A. Energy pattern neighbourhood'
Tfl, product cooling supply temp | 268.15 | K | [13 empty] | Tfl, product cooling supply temp | 268.15 | K
Tfl, floor cooling supply temp | 285.15 | K | [13 empty] | Tfl, floor cooling supply temp | 285.15 | K
Tfl return product cooling | 273.15 | K | [13 empty] | Tfl return product cooling | 273.15 | K
Tfl return floor cooling | 295.15 | K | [13 empty] | Tfl return floor cooling | 295.15 | K
Efficiency condenser/evaporator | 90% | [14 empty] | Efficiency condenser/evaporator | 90%
18 january coldest weekday 2012-2022 | [15 empty] | 24 July warmest weekday 2012-2022
water/water HE3; ε | 80% | [14 empty] | water/water HE3; ε | 80%
HP3 - active cooling of supermarket product cooling
|  |  |  | Tfl return average | [11 empty] | HP3 - active cooling of supermarket product cooling
WINTERDAY | Cooling demands total NBH | Product cooling | Cooling demands supermarket | Th,o ev | Th,i ev | T3 = Tev | Tc,o condenser | Tc,i condenser | T1 = Tcon | Qcon HP3 | COPh | Win |  |  |  | Summer day | Cooling demands NBH total | Cooling demands supermarket | Product cooling | Space cooling | Th,o ev | Th,i ev | T3 = Tev | Tc,o condenser | Tc,i condenser | T1 = Tcon | Qcon HP3 | COPh | Win
18 January | kW | % | kW | C | C | C | C | C | C | kW | - | kW |  |  |  | 24 July | kW | kW | % | % | C | C | C | C | C | C | kW | - | kW
0:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 0:00 | 466.113 | 466.113 | 100% | 0% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
1:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 1:00 | 466.113 | 466.113 | 100% | 0% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
2:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 2:00 | 466.113 | 466.113 | 100% | 0% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
3:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 3:00 | 466.113 | 466.113 | 100% | 0% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
4:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 4:00 | 466.113 | 466.113 | 100% | 0% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
5:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 5:00 | 466.113 | 466.113 | 100% | 0% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
6:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 6:00 | 872.9029 | 466.113 | 53.4% | 46.6% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
7:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 7:00 | 1564.4458 | 466.113 | 29.79% | 70.21% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
8:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 8:00 | 2215.3096 | 466.113 | 21.04% | 78.96% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
9:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 9:00 | 2784.8155 | 466.113 | 16.74% | 83.26% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
10:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 10:00 | 3150.9264 | 466.113 | 14.79% | 85.21% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
11:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 11:00 | 3720.4322 | 466.113 | 12.53% | 87.47% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
12:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 12:00 | 4045.8641 | 466.113 | 11.52% | 88.48% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
13:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 13:00 | 4493.333 | 466.113 | 10.37% | 89.63% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
14:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 14:00 | 4818.7649 | 466.113 | 9.673% | 90.33% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
15:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 15:00 | 4981.4809 | 466.113 | 9.357% | 90.64% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
16:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 16:00 | 4940.8019 | 466.113 | 9.434% | 90.57% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
17:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 17:00 | 4656.049 | 466.113 | 10.01% | 89.99% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
18:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 18:00 | 4534.012 | 466.113 | 10.28% | 89.72% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
19:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 19:00 | 1149.8837 | 466.113 | 40.54% | 59.46% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
20:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 20:00 | 1011.593 | 466.113 | 46.08% | 53.92% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
21:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 21:00 | 880.9851 | 466.113 | 52.91% | 47.09% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
22:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 22:00 | 857.9367 | 466.113 | 54.33% | 45.67% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
23:00 | 466.113 | 100% | 466.113 | -5 | 0 | -5.5556 | 19.75 | 2.75 | 21.6389 | 548.0794 | 6.6866 | 81.9664 |  |  |  | 23:00 | 819.5226 | 466.113 | 56.88% | 43.12% | -5 | 0 | -5.5556 | 28.25 | 11.25 | 30.1389 | 571.8626 | 5.4077 | 105.7496
HP5a-.. active cooling (space cooling) | [15 empty] | HP5a-.. active cooling (space cooling)
not applicable in winter | [15 empty] | Summer day | Cooling demands NBH total | Cooling demands NBH | Product cooling | Space cooling | Qev HP5 | Th,i | Th,o | T3 | Tc,i | Tc,o | T1 | Qcon | COP | Win
[16 empty] | 24 July | kW | kW | % | % | kW | C | C | C | C | C | C | kW |  | kW
[16 empty] | 0:00 | 466.113 | 0 | 100% | 0% | 0 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 0 | 10.2658 | 0
[16 empty] | 1:00 | 466.113 | 0 | 100% | 0% | 0 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 0 | 10.2658 | 0
[16 empty] | 2:00 | 466.113 | 0 | 100% | 0% | 0 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 0 | 10.2658 | 0
[16 empty] | 3:00 | 466.113 | 0 | 100% | 0% | 0 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 0 | 10.2658 | 0
[16 empty] | 4:00 | 466.113 | 0 | 100% | 0% | 0 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 0 | 10.2658 | 0
[16 empty] | 5:00 | 466.113 | 0 | 100% | 0% | 0 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 0 | 10.2658 | 0
[16 empty] | 6:00 | 872.9029 | 406.7899 | 53.4% | 46.6% | 406.7899 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 43.9022 | 10.2658 | 4.2765
[16 empty] | 7:00 | 1564.4458 | 1098.3327 | 29.79% | 70.21% | 1098.3327 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 118.536 | 10.2658 | 11.5467
[16 empty] | 8:00 | 2215.3096 | 1749.1966 | 21.04% | 78.96% | 1749.1966 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 188.7796 | 10.2658 | 18.3892
[16 empty] | 9:00 | 2784.8155 | 2318.7024 | 16.74% | 83.26% | 2318.7024 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 250.2427 | 10.2658 | 24.3763
[16 empty] | 10:00 | 3150.9264 | 2684.8133 | 14.79% | 85.21% | 2684.8133 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 289.7547 | 10.2658 | 28.2252
[16 empty] | 11:00 | 3720.4322 | 3254.3192 | 12.53% | 87.47% | 3254.3192 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 351.2178 | 10.2658 | 34.2124
[16 empty] | 12:00 | 4045.8641 | 3579.7511 | 11.52% | 88.48% | 3579.7511 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 386.3396 | 10.2658 | 37.6336
[16 empty] | 13:00 | 4493.333 | 4027.22 | 10.37% | 89.63% | 4027.22 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 434.6321 | 10.2658 | 42.3378
[16 empty] | 14:00 | 4818.7649 | 4352.6519 | 9.673% | 90.33% | 4352.6519 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 469.7539 | 10.2658 | 45.759
[16 empty] | 15:00 | 4981.4809 | 4515.3679 | 9.357% | 90.64% | 4515.3679 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 487.3148 | 10.2658 | 47.4697
[16 empty] | 16:00 | 4940.8019 | 4474.6889 | 9.434% | 90.57% | 4474.6889 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 482.9245 | 10.2658 | 47.042
[16 empty] | 17:00 | 4656.049 | 4189.936 | 10.01% | 89.99% | 4189.936 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 452.193 | 10.2658 | 44.0484
[16 empty] | 18:00 | 4534.012 | 4067.899 | 10.28% | 89.72% | 4067.899 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 439.0223 | 10.2658 | 42.7655
[16 empty] | 19:00 | 1149.8837 | 683.7707 | 40.54% | 59.46% | 683.7707 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 73.795 | 10.2658 | 7.1884
[16 empty] | 20:00 | 1011.593 | 545.48 | 46.08% | 53.92% | 545.48 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 58.8702 | 10.2658 | 5.7346
[16 empty] | 21:00 | 880.9851 | 414.8721 | 52.91% | 47.09% | 414.8721 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 44.7745 | 10.2658 | 4.3615
[16 empty] | 22:00 | 857.9367 | 391.8236 | 54.33% | 45.67% | 391.8236 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 42.287 | 10.2658 | 4.1192
[16 empty] | 23:00 | 819.5226 | 353.4096 | 56.88% | 43.12% | 353.4096 | 22 | 12 | 10.8889 | 11.25 | 28.25 | 30.1389 | 38.1412 | 10.2658 | 3.7154
VF | [15 empty] | VF
QHE3 winter photoperiod | 0 | J m-2 s-1 | W m-2 | [12 empty] | QHE3 winter photoperiod | 61.443 | J m-2 s-1 | W m-2
QHE3 winter dark period | 0 | J m-2 s-1 | W m-2 | [12 empty] | QHE3 winter dark period | 41.9659 | J m-2 s-1 | W m-2
WINTERDAY | QHE3 | [14 empty] | WINTERDAY | QHE3
18 January | kW | [14 empty] | 18 January | kW
0:00 | 0 | [14 empty] | 0:00 | 2368.413
1:00 | 0 | [14 empty] | 1:00 | 2368.413
2:00 | 0 | [14 empty] | 2:00 | 2368.413
3:00 | 0 | [14 empty] | 3:00 | 1617.638
4:00 | 0 | [14 empty] | 4:00 | 1617.638
5:00 | 0 | [14 empty] | 5:00 | 1617.638
6:00 | 0 | [14 empty] | 6:00 | 1617.638
7:00 | 0 | [14 empty] | 7:00 | 1617.638
8:00 | 0 | [14 empty] | 8:00 | 1617.638
9:00 | 0 | [14 empty] | 9:00 | 1617.638
10:00 | 0 | [14 empty] | 10:00 | 1617.638
11:00 | 0 | [14 empty] | 11:00 | 2368.413
12:00 | 0 | [14 empty] | 12:00 | 2368.413
13:00 | 0 | [14 empty] | 13:00 | 2368.413
14:00 | 0 | [14 empty] | 14:00 | 2368.413
15:00 | 0 | [14 empty] | 15:00 | 2368.413
16:00 | 0 | [14 empty] | 16:00 | 2368.413
17:00 | 0 | [14 empty] | 17:00 | 2368.413
18:00 | 0 | [14 empty] | 18:00 | 2368.413
19:00 | 0 | [14 empty] | 19:00 | 2368.413
20:00 | 0 | [14 empty] | 20:00 | 2368.413
21:00 | 0 | [14 empty] | 21:00 | 2368.413
22:00 | 0 | [14 empty] | 22:00 | 2368.413
23:00 | 0 | [14 empty] | 23:00 | 2368.413
ATES | [15 empty] | ATES
Negative is stored, positive extracted ATES | [15 empty] | Negative is stored, positive extracted ATES
WINTERDAY | Qev HP3 | Qlosses uLT | Total demand | QVF | Qcon HP4 (NBH cooling) | QHE4 extracted/stored | Flow rate m ATES-side | Pump ATES | [7 empty] | Summer day | Qev HP3 | Qlosses uLT | Total demand | QVF | Qcon HP4+5 (NBH cooling) | QHE4 extracted/stored | Flow rate m ATES-side | Pump ATES
18 January | kW | kW | KW | kW | kW | kW | kg/s | kJ/s | [7 empty] | 24 July | kW | kW | KW | kW | kW | kW | kg/s | kJ/s
0:00 | 3098.1956 | 464.7293 | 3562.9249 | 0 | 548.0794 | 3014.8455 | 42.3862 | 0.32181 | [7 empty] | 0:00 | 410.9355 | 61.6403 | 472.5758 | 2368.413 | 571.8626 | -2467.6997 | -34.6938 | 0.2634
1:00 | 2576.1535 | 386.423 | 2962.5765 | 0 | 548.0794 | 2414.4971 | 33.9458 | 0.25772 | [7 empty] | 1:00 | 332.9656 | 49.9448 | 382.9105 | 2368.413 | 571.8626 | -2557.3651 | -35.9544 | 0.27297
2:00 | 2548.2801 | 382.242 | 2930.5221 | 0 | 548.0794 | 2382.4426 | 33.4951 | 0.2543 | [7 empty] | 2:00 | 334.9271 | 50.2391 | 385.1662 | 2368.413 | 571.8626 | -2555.1094 | -35.9227 | 0.27273
3:00 | 2742.1935 | 411.329 | 3153.5225 | 0 | 548.0794 | 2605.443 | 36.6303 | 0.27811 | [7 empty] | 3:00 | 340.8117 | 51.1217 | 391.9334 | 1617.638 | 571.8626 | -1797.5672 | -25.2723 | 0.19187
4:00 | 2939.7047 | 440.9557 | 3380.6604 | 0 | 548.0794 | 2832.581 | 39.8237 | 0.30235 | [7 empty] | 4:00 | 357.4845 | 53.6227 | 411.1071 | 1617.638 | 571.8626 | -1778.3935 | -25.0027 | 0.18983
5:00 | 3148.177 | 472.2265 | 3620.4035 | 0 | 548.0794 | 3072.3241 | 43.1943 | 0.32794 | [7 empty] | 5:00 | 573.2501 | 85.9875 | 659.2376 | 1617.638 | 571.8626 | -1530.263 | -21.5142 | 0.16334
6:00 | 4324.3181 | 648.6477 | 4972.9658 | 0 | 548.0794 | 4424.8864 | 62.2102 | 0.47231 | [7 empty] | 6:00 | 972.4166 | 145.8625 | 1118.2791 | 1617.638 | 615.7648 | -1115.1238 | -15.6777 | 0.11903
7:00 | 6838.8911 | 1025.8337 | 7864.7248 | 0 | 548.0794 | 7316.6453 | 102.8659 | 0.78098 | [7 empty] | 7:00 | 1026.8484 | 154.0273 | 1180.8756 | 1617.638 | 690.3986 | -1127.161 | -15.8469 | 0.12031
8:00 | 8461.1548 | 1269.1732 | 9730.328 | 0 | 548.0794 | 9182.2486 | 129.0947 | 0.98012 | [7 empty] | 8:00 | 1100.8952 | 165.1343 | 1266.0295 | 1617.638 | 760.6422 | -1112.2507 | -15.6373 | 0.11872
9:00 | 9120.9845 | 1368.1477 | 10489.1322 | 0 | 548.0794 | 9941.0528 | 139.7629 | 1.0611 | [7 empty] | 9:00 | 1133.2601 | 169.989 | 1303.2491 | 1617.638 | 822.1053 | -1136.4943 | -15.9782 | 0.12131
10:00 | 8523.78 | 1278.567 | 9802.347 | 0 | 548.0794 | 9254.2676 | 130.1072 | 0.9878 | [7 empty] | 10:00 | 984.1856 | 147.6278 | 1131.8135 | 1617.638 | 861.6173 | -1347.4419 | -18.9439 | 0.14383
11:00 | 7747.2388 | 1162.0858 | 8909.3246 | 0 | 548.0794 | 8361.2451 | 117.5521 | 0.89248 | [7 empty] | 11:00 | 985.1664 | 147.775 | 1132.9413 | 2368.413 | 923.0804 | -2158.5521 | -30.3474 | 0.2304
12:00 | 7567.5549 | 1135.1332 | 8702.6881 | 0 | 548.0794 | 8154.6087 | 114.647 | 0.87043 | [7 empty] | 12:00 | 1011.6467 | 151.747 | 1163.3937 | 2368.413 | 958.2022 | -2163.2215 | -30.4131 | 0.2309
13:00 | 7352.1047 | 1102.8157 | 8454.9204 | 0 | 548.0794 | 7906.8409 | 111.1635 | 0.84398 | [7 empty] | 13:00 | 884.1488 | 132.6223 | 1016.7711 | 2368.413 | 1006.4947 | -2358.1365 | -33.1534 | 0.25171
14:00 | 7441.1325 | 1116.1699 | 8557.3023 | 0 | 548.0794 | 8009.2229 | 112.603 | 0.85491 | [7 empty] | 14:00 | 772.8333 | 115.925 | 888.7584 | 2368.413 | 1041.6165 | -2521.2711 | -35.447 | 0.26912
15:00 | 7672.7422 | 1150.9113 | 8823.6535 | 0 | 548.0794 | 8275.574 | 116.3476 | 0.88334 | [7 empty] | 15:00 | 851.784 | 127.7676 | 979.5516 | 2368.413 | 1059.1774 | -2448.0388 | -34.4174 | 0.2613
16:00 | 7911.9427 | 1186.7914 | 9098.7341 | 0 | 548.0794 | 8550.6546 | 120.215 | 0.9127 | [7 empty] | 16:00 | 1146.0099 | 171.9015 | 1317.9113 | 2368.413 | 1054.7871 | -2105.2888 | -29.5986 | 0.22472
17:00 | 9248.1045 | 1387.2157 | 10635.3202 | 0 | 548.0794 | 10087.2408 | 141.8181 | 1.0767 | [7 empty] | 17:00 | 1744.7596 | 261.7139 | 2006.4735 | 2368.413 | 1024.0556 | -1385.9951 | -19.4859 | 0.14794
18:00 | 10230.8339 | 1534.6251 | 11765.459 | 0 | 548.0794 | 11217.3796 | 157.7069 | 1.1973 | [7 empty] | 18:00 | 1733.4809 | 260.0221 | 1993.503 | 2368.413 | 1010.8849 | -1385.7949 | -19.4831 | 0.14792
19:00 | 9335.4628 | 1400.3194 | 10735.7822 | 0 | 548.0794 | 10187.7027 | 143.2306 | 1.0874 | [7 empty] | 19:00 | 1444.6491 | 216.6974 | 1661.3465 | 2368.413 | 645.6576 | -1352.7241 | -19.0182 | 0.14439
20:00 | 8755.3004 | 1313.2951 | 10068.5955 | 0 | 548.0794 | 9520.5161 | 133.8505 | 1.0162 | [7 empty] | 20:00 | 1231.3354 | 184.7003 | 1416.0357 | 2368.413 | 630.7327 | -1583.1101 | -22.2572 | 0.16898
21:00 | 7887.7841 | 1183.1676 | 9070.9517 | 0 | 548.0794 | 8522.8722 | 119.8244 | 0.90973 | [7 empty] | 21:00 | 1030.281 | 154.5422 | 1184.8232 | 2368.413 | 616.6371 | -1800.2269 | -25.3097 | 0.19216
22:00 | 6346.325 | 951.9488 | 7298.2738 | 0 | 548.0794 | 6750.1944 | 94.9021 | 0.72052 | [7 empty] | 22:00 | 865.5145 | 129.8272 | 995.3417 | 2368.413 | 614.1496 | -1987.2209 | -27.9387 | 0.21212
23:00 | 4589.6918 | 688.4538 | 5278.1456 | 0 | 548.0794 | 4730.0662 | 66.5008 | 0.50489 | [7 empty] | 23:00 | 598.7497 | 89.8125 | 688.5621 | 2368.413 | 610.0038 | -2289.8547 | -32.1934 | 0.24442
Vertical farm | [15 empty] | Vertical farm
| Light (16h) | Dark (8h) | [14 empty] | Light (16h) | Dark (8h)
LED | 35242.5345 | 0 | kWh d-1 | [12 empty] | LED | 35242.5345 | 0 | kWh d-1
| 2202.6584 | 0 | kW | [13 empty] | 2202.6584 | 0 | kW
HP1 | 2713.0067 | 1052.8049 | kWh d-1 | [12 empty] | HP1 | 6176.3267 | 2446.2367 | kWh d-1
| 169.5629 | 131.6006 | kW | [13 empty] | 386.0204 | 305.7796 | kW
Fans, pumps | 2637.4338 | 1314.5342 | kWh d-1 | [12 empty] | Fans, pumps | 2637.4338 | 1314.5342 | kWh d-1
| 164.8396 | 164.3168 | kW | [13 empty] | 164.8396 | 164.3168 | kW
Electricity profile | [15 empty] | Electricity profile
| VF fans, pumps | VF HP1 | VF LED | Total | [12 empty] | VF fans, pumps | VF HP1 | VF LED | Total
| kW | kW | kW | kW | [12 empty] | kW | kW | kW | kW
0:00 | 164.8396 | 169.5629 | 2202.6584 | 2537.0609 | [11 empty] | 0:00 | 164.8396 | 386.0204 | 2202.6584 | 2753.5184
1:00 | 164.8396 | 169.5629 | 2202.6584 | 2537.0609 | [11 empty] | 1:00 | 164.8396 | 386.0204 | 2202.6584 | 2753.5184
2:00 | 164.8396 | 169.5629 | 2202.6584 | 2537.0609 | [11 empty] | 2:00 | 164.8396 | 386.0204 | 2202.6584 | 2753.5184
3:00 | 164.3168 | 169.5629 | 2202.6584 | 2536.5381 | [11 empty] | 3:00 | 164.3168 | 386.0204 | 2202.6584 | 2752.9956
4:00 | 164.3168 | 131.6006 | 0 | 295.9174 | [11 empty] | 4:00 | 164.3168 | 305.7796 | 0 | 470.0964
5:00 | 164.3168 | 131.6006 | 0 | 295.9174 | [11 empty] | 5:00 | 164.3168 | 305.7796 | 0 | 470.0964
6:00 | 164.3168 | 131.6006 | 0 | 295.9174 | [11 empty] | 6:00 | 164.3168 | 305.7796 | 0 | 470.0964
7:00 | 164.3168 | 131.6006 | 0 | 295.9174 | [11 empty] | 7:00 | 164.3168 | 305.7796 | 0 | 470.0964
8:00 | 164.3168 | 169.5629 | 2202.6584 | 2536.5381 | [11 empty] | 8:00 | 164.3168 | 386.0204 | 2202.6584 | 2752.9956
9:00 | 164.3168 | 169.5629 | 2202.6584 | 2536.5381 | [11 empty] | 9:00 | 164.3168 | 386.0204 | 2202.6584 | 2752.9956
10:00 | 164.3168 | 169.5629 | 2202.6584 | 2536.5381 | [11 empty] | 10:00 | 164.3168 | 386.0204 | 2202.6584 | 2752.9956
11:00 | 164.8396 | 169.5629 | 2202.6584 | 2537.0609 | [11 empty] | 11:00 | 164.8396 | 386.0204 | 2202.6584 | 2753.5184
12:00 | 164.8396 | 169.5629 | 2202.6584 | 2537.0609 | [11 empty] | 12:00 | 164.8396 | 386.0204 | 2202.6584 | 2753.5184
13:00 | 164.8396 | 169.5629 | 2202.6584 | 2537.0609 | [11 empty] | 13:00 | 164.8396 | 386.0204 | 2202.6584 | 2753.5184
14:00 | 164.8396 | 169.5629 | 2202.6584 | 2537.0609 | [11 empty] | 14:00 | 164.8396 | 386.0204 | 2202.6584 | 2753.5184
15:00 | 164.8396 | 169.5629 | 2202.6584 | 2537.0609 | [11 empty] | 15:00 | 164.8396 | 386.0204 | 2202.6584 | 2753.5184
16:00 | 164.8396 | 131.6006 | 0 | 296.4402 | [11 empty] | 16:00 | 164.8396 | 305.7796 | 0 | 470.6192
17:00 | 164.8396 | 131.6006 | 0 | 296.4402 | [11 empty] | 17:00 | 164.8396 | 305.7796 | 0 | 470.6192
18:00 | 164.8396 | 131.6006 | 0 | 296.4402 | [11 empty] | 18:00 | 164.8396 | 305.7796 | 0 | 470.6192
19:00 | 164.8396 | 131.6006 | 0 | 296.4402 | [11 empty] | 19:00 | 164.8396 | 305.7796 | 0 | 470.6192
20:00 | 164.8396 | 169.5629 | 2202.6584 | 2537.0609 | [11 empty] | 20:00 | 164.8396 | 386.0204 | 2202.6584 | 2753.5184
21:00 | 164.8396 | 169.5629 | 2202.6584 | 2537.0609 | [11 empty] | 21:00 | 164.8396 | 386.0204 | 2202.6584 | 2753.5184
22:00 | 164.8396 | 169.5629 | 2202.6584 | 2537.0609 | [11 empty] | 22:00 | 164.8396 | 386.0204 | 2202.6584 | 2753.5184
23:00 | 164.8396 | 169.5629 | 2202.6584 | 2537.0609 | [11 empty] | 23:00 | 164.8396 | 386.0204 | 2202.6584 | 2753.5184
Pumps DHN | [15 empty] | Pumps DHN
| LT Grid | [15 empty] | LT Grid
Month | Q | Q | m | m | Pumps LT DHN | [10 empty] | Month | Q | Q | m | m | Pumps LT DHN
| kW | MJ/h | kg / h | m3/h | kW | [11 empty] | kW | MJ/h | kg / h | m3/h | kW
0:00 | 3562.9249 | 12826.5298 | 50091.7353 | 50.2425 | 10.0485 | [10 empty] | 0:00 | 472.5758 | 1701.273 | 6644.0196 | 6.664 | 1.3328
1:00 | 2962.5765 | 10665.2754 | 41651.34 | 41.7767 | 8.3553 | [10 empty] | 1:00 | 382.9105 | 1378.4777 | 5383.4001 | 5.3996 | 1.0799
2:00 | 2930.5221 | 10549.8795 | 41200.6816 | 41.3247 | 8.2649 | [10 empty] | 2:00 | 385.1662 | 1386.5984 | 5415.1138 | 5.4314 | 1.0863
3:00 | 3153.5225 | 11352.6809 | 44335.8801 | 44.4693 | 8.8939 | [10 empty] | 3:00 | 391.9334 | 1410.9603 | 5510.2549 | 5.5268 | 1.1054
4:00 | 3380.6604 | 12170.3776 | 47529.2492 | 47.6723 | 9.5345 | [10 empty] | 4:00 | 411.1071 | 1479.9857 | 5779.8213 | 5.7972 | 1.1594
5:00 | 3620.4035 | 13033.4528 | 50899.8361 | 51.053 | 10.2106 | [10 empty] | 5:00 | 659.2376 | 2373.2555 | 9268.328 | 9.2962 | 1.8592
6:00 | 4972.9658 | 17902.6769 | 69915.7265 | 70.1261 | 14.0252 | [10 empty] | 6:00 | 1118.2791 | 4025.8046 | 15722.0654 | 15.7694 | 3.1539
7:00 | 7864.7248 | 28313.0092 | 110571.4314 | 110.9041 | 22.1808 | [10 empty] | 7:00 | 1180.8756 | 4251.1523 | 16602.1205 | 16.6521 | 3.3304
8:00 | 9730.328 | 35029.181 | 136800.2481 | 137.2119 | 27.4424 | [10 empty] | 8:00 | 1266.0295 | 4557.7062 | 17799.3126 | 17.8529 | 3.5706
9:00 | 10489.1322 | 37760.8759 | 147468.3979 | 147.9121 | 29.5824 | [10 empty] | 9:00 | 1303.2491 | 4691.6967 | 18322.5886 | 18.3777 | 3.6755
10:00 | 9802.347 | 35288.4493 | 137812.7745 | 138.2275 | 27.6455 | [10 empty] | 10:00 | 1131.8135 | 4074.5285 | 15912.3476 | 15.9602 | 3.192
11:00 | 8909.3246 | 32073.5685 | 125257.6284 | 125.6345 | 25.1269 | [10 empty] | 11:00 | 1132.9413 | 4078.5888 | 15928.2044 | 15.9761 | 3.1952
12:00 | 8702.6881 | 31329.6772 | 122352.493 | 122.7207 | 24.5441 | [10 empty] | 12:00 | 1163.3937 | 4188.2173 | 16356.3394 | 16.4056 | 3.2811
13:00 | 8454.9204 | 30437.7133 | 118869.0862 | 119.2268 | 23.8454 | [10 empty] | 13:00 | 1016.7711 | 3660.3761 | 14294.949 | 14.338 | 2.8676
14:00 | 8557.3023 | 30806.2884 | 120308.4909 | 120.6705 | 24.1341 | [10 empty] | 14:00 | 888.7584 | 3199.5301 | 12495.1967 | 12.5328 | 2.5066
15:00 | 8823.6535 | 31765.1525 | 124053.1644 | 124.4264 | 24.8853 | [10 empty] | 15:00 | 979.5516 | 3526.3856 | 13771.673 | 13.8131 | 2.7626
16:00 | 9098.7341 | 32755.4426 | 127920.5666 | 128.3055 | 25.6611 | [10 empty] | 16:00 | 1317.9113 | 4744.4808 | 18528.7276 | 18.5845 | 3.7169
17:00 | 10635.3202 | 38287.1528 | 149523.6786 | 149.9736 | 29.9947 | [10 empty] | 17:00 | 2006.4735 | 7223.3046 | 28209.3337 | 28.2942 | 5.6588
18:00 | 11765.459 | 42355.6525 | 165412.4821 | 165.9102 | 33.182 | [10 empty] | 18:00 | 1993.503 | 7176.6109 | 28026.98 | 28.1113 | 5.6223
19:00 | 10735.7822 | 38648.8158 | 150936.0895 | 151.3903 | 30.2781 | [10 empty] | 19:00 | 1661.3465 | 5980.8475 | 23357.138 | 23.4274 | 4.6855
20:00 | 10068.5955 | 36246.9438 | 141556.0047 | 141.982 | 28.3964 | [10 empty] | 20:00 | 1416.0357 | 5097.7284 | 19908.2735 | 19.9682 | 3.9936
21:00 | 9070.9517 | 32655.4261 | 127529.9697 | 127.9137 | 25.5827 | [10 empty] | 21:00 | 1184.8232 | 4265.3634 | 16657.6195 | 16.7077 | 3.3415
22:00 | 7298.2738 | 26273.7857 | 102607.606 | 102.9164 | 20.5833 | [10 empty] | 22:00 | 995.3417 | 3583.2301 | 13993.6689 | 14.0358 | 2.8072
23:00 | 5278.1456 | 19001.3242 | 74206.2988 | 74.4296 | 14.8859 | [10 empty] | 23:00 | 688.5621 | 2478.8237 | 9680.6061 | 9.7097 | 1.9419
Total | [15 empty] | Total
Electricity profile | [15 empty] | Electricity profile
| VF fans, pumps | VF HP1 | VF LED | NBH heating (HP3) | ATES pump | DHN pumps | NBH cooling (HP4) | URE | EV charging | Total | [6 empty] | VF fans, pumps | VF HP1 | VF LED | NBH heating (HP3) | ATES pump | DHN pumps | NBH cooling (HP4+5) | URE | EV charging | Total
| kW | kW | kW | kW | kW | kW | kW | kW | kW | kW | [6 empty] | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW
0:00 | 164.8396 | 169.5629 | 2202.6584 | 1896.5987 | 0.32181 | 10.0485 | 81.9664 | 277.3137 | 44.3467 | 4847.6568 | [5 empty] | 0:00 | 164.8396 | 386.0204 | 2202.6584 | 147.3809 | 0.2634 | 1.3328 | 105.7496 | 288.9848 | 44.3467 | 3341.5766
1:00 | 164.8396 | 169.5629 | 2202.6584 | 1577.0242 | 0.25772 | 8.3553 | 81.9664 | 237.5549 | 38.9714 | 4481.1908 | [5 empty] | 1:00 | 164.8396 | 386.0204 | 2202.6584 | 119.4172 | 0.27297 | 1.0799 | 105.7496 | 246.2969 | 38.9714 | 3265.3064
2:00 | 164.8396 | 169.5629 | 2202.6584 | 1559.9611 | 0.2543 | 8.2649 | 81.9664 | 217.0093 | 30.9083 | 4435.4254 | [5 empty] | 2:00 | 164.8396 | 386.0204 | 2202.6584 | 120.1207 | 0.27273 | 1.0863 | 105.7496 | 219.9491 | 30.9083 | 3231.6052
3:00 | 164.3168 | 169.5629 | 2202.6584 | 1678.6676 | 0.27811 | 8.8939 | 81.9664 | 206.4166 | 25.533 | 4538.2936 | [5 empty] | 3:00 | 164.3168 | 386.0204 | 2202.6584 | 122.2312 | 0.19187 | 1.1054 | 105.7496 | 204.6696 | 25.533 | 3212.4762
4:00 | 164.3168 | 131.6006 | 0 | 1799.5766 | 0.30235 | 9.5345 | 81.9664 | 200.7646 | 18.8138 | 2406.8755 | [5 empty] | 4:00 | 164.3168 | 305.7796 | 0 | 128.2108 | 0.18983 | 1.1594 | 105.7496 | 200.8105 | 18.8138 | 925.0303
5:00 | 164.3168 | 131.6006 | 0 | 1927.1954 | 0.32794 | 10.2106 | 81.9664 | 213.2419 | 13.4384 | 2542.2981 | [5 empty] | 5:00 | 164.3168 | 305.7796 | 0 | 205.5946 | 0.16334 | 1.8592 | 105.7496 | 208.5809 | 13.4384 | 1005.4823
6:00 | 164.3168 | 131.6006 | 0 | 2647.1847 | 0.47231 | 14.0252 | 81.9664 | 253.9743 | 8.063 | 3301.6035 | [5 empty] | 6:00 | 164.3168 | 305.7796 | 0 | 348.7545 | 0.11903 | 3.1539 | 110.0261 | 233.9492 | 8.063 | 1174.1621
7:00 | 164.3168 | 131.6006 | 0 | 4186.5117 | 0.78098 | 22.1808 | 81.9664 | 322.9072 | 17.4699 | 4927.7344 | [5 empty] | 7:00 | 164.3168 | 305.7796 | 0 | 368.2763 | 0.12031 | 3.3304 | 117.2962 | 283.302 | 17.4699 | 1259.8916
8:00 | 164.3168 | 169.5629 | 2202.6584 | 5179.6004 | 0.98012 | 27.4424 | 81.9664 | 359.4094 | 29.5645 | 8215.5013 | [5 empty] | 8:00 | 164.3168 | 386.0204 | 2202.6584 | 394.833 | 0.11872 | 3.5706 | 124.1387 | 347.1998 | 29.5645 | 3652.4209
9:00 | 164.3168 | 169.5629 | 2202.6584 | 5583.5233 | 1.0611 | 29.5824 | 81.9664 | 376.9609 | 41.659 | 8651.2914 | [5 empty] | 9:00 | 164.3168 | 386.0204 | 2202.6584 | 406.4406 | 0.12131 | 3.6755 | 130.1259 | 393.9319 | 41.659 | 3728.9499
10:00 | 164.3168 | 169.5629 | 2202.6584 | 5217.9372 | 0.9878 | 27.6455 | 81.9664 | 381.2817 | 34.9398 | 8281.2965 | [5 empty] | 10:00 | 164.3168 | 386.0204 | 2202.6584 | 352.9755 | 0.14383 | 3.192 | 133.9748 | 402.8935 | 34.9398 | 3681.115
11:00 | 164.8396 | 169.5629 | 2202.6584 | 4742.5679 | 0.89248 | 25.1269 | 81.9664 | 370.5403 | 28.2206 | 7786.3756 | [5 empty] | 11:00 | 164.8396 | 386.0204 | 2202.6584 | 353.3272 | 0.2304 | 3.1952 | 139.9619 | 407.6655 | 28.2206 | 3686.1193
12:00 | 164.8396 | 169.5629 | 2202.6584 | 4632.5722 | 0.87043 | 24.5441 | 81.9664 | 365.423 | 22.8453 | 7665.2824 | [5 empty] | 12:00 | 164.8396 | 386.0204 | 2202.6584 | 362.8243 | 0.2309 | 3.2811 | 143.3832 | 415.1209 | 22.8453 | 3701.2041
13:00 | 164.8396 | 169.5629 | 2202.6584 | 4500.6817 | 0.84398 | 23.8454 | 81.9664 | 367.7989 | 25.533 | 7537.7303 | [5 empty] | 13:00 | 164.8396 | 386.0204 | 2202.6584 | 317.0975 | 0.25171 | 2.8676 | 148.0874 | 404.346 | 25.533 | 3651.7016
14:00 | 164.8396 | 169.5629 | 2202.6584 | 4555.1811 | 0.85491 | 24.1341 | 81.9664 | 360.3372 | 24.1891 | 7583.7238 | [5 empty] | 14:00 | 164.8396 | 386.0204 | 2202.6584 | 277.1746 | 0.26912 | 2.5066 | 151.5086 | 401.2686 | 24.1891 | 3610.435
15:00 | 164.8396 | 169.5629 | 2202.6584 | 4696.9639 | 0.88334 | 24.8853 | 81.9664 | 359.8236 | 24.1891 | 7725.7726 | [5 empty] | 15:00 | 164.8396 | 386.0204 | 2202.6584 | 305.49 | 0.2613 | 2.7626 | 153.2192 | 405.8541 | 24.1891 | 3645.2948
16:00 | 164.8396 | 131.6006 | 0 | 4843.3934 | 0.9127 | 25.6611 | 81.9664 | 365.2218 | 26.8768 | 5640.4724 | [5 empty] | 16:00 | 164.8396 | 305.7796 | 0 | 411.0133 | 0.22472 | 3.7169 | 152.7916 | 450.9235 | 26.8768 | 1516.166
17:00 | 164.8396 | 131.6006 | 0 | 5661.3414 | 1.0767 | 29.9947 | 81.9664 | 406.2677 | 14.4721 | 6491.5593 | [5 empty] | 17:00 | 164.8396 | 305.7796 | 0 | 625.7532 | 0.14794 | 5.6588 | 149.798 | 542.3265 | 14.4721 | 1808.7758
18:00 | 164.8396 | 131.6006 | 0 | 6262.9314 | 1.1973 | 33.182 | 81.9664 | 522.6252 | 40.3152 | 7238.6578 | [5 empty] | 18:00 | 164.8396 | 305.7796 | 0 | 621.7081 | 0.14792 | 5.6223 | 148.515 | 542.0794 | 40.3152 | 1829.0071
19:00 | 164.8396 | 131.6006 | 0 | 5714.8188 | 1.0874 | 30.2781 | 81.9664 | 530.3969 | 52.4098 | 6707.3977 | [5 empty] | 19:00 | 164.8396 | 305.7796 | 0 | 518.1194 | 0.14439 | 4.6855 | 112.938 | 505.6715 | 52.4098 | 1664.5878
20:00 | 164.8396 | 169.5629 | 2202.6584 | 5359.6653 | 1.0162 | 28.3964 | 81.9664 | 502.0107 | 48.3782 | 8558.4942 | [5 empty] | 20:00 | 164.8396 | 386.0204 | 2202.6584 | 441.615 | 0.16898 | 3.9936 | 111.4841 | 465.7749 | 48.3782 | 3824.9334
21:00 | 164.8396 | 169.5629 | 2202.6584 | 4828.6044 | 0.90973 | 25.5827 | 81.9664 | 461.4897 | 44.3467 | 7979.9607 | [5 empty] | 21:00 | 164.8396 | 386.0204 | 2202.6584 | 369.5074 | 0.19216 | 3.3415 | 110.1111 | 416.2452 | 44.3467 | 3697.2626
22:00 | 164.8396 | 169.5629 | 2202.6584 | 3884.9813 | 0.72052 | 20.5833 | 81.9664 | 424.7429 | 40.3152 | 6990.3705 | [5 empty] | 22:00 | 164.8396 | 386.0204 | 2202.6584 | 310.4144 | 0.21212 | 2.8072 | 109.8688 | 384.2443 | 40.3152 | 3601.3804
23:00 | 164.8396 | 169.5629 | 2202.6584 | 2809.6365 | 0.50489 | 14.8859 | 81.9664 | 379.8485 | 43.0029 | 5866.9061 | [5 empty] | 23:00 | 164.8396 | 386.0204 | 2202.6584 | 214.7399 | 0.24442 | 1.9419 | 109.4649 | 340.0549 | 43.0029 | 3462.9674
Heat balance | [15 empty] | Heat balance
| Heat demand | Qlosses grid total | VF produce (Qhe3) | NBH heating Win HP3 | ATES | NBH cooling (Qcon HP3) | Total supply | Tot demand | [8 empty] | Heat demand | Qlosses grid total | VF produce (Qhe3) | NBH heating Win HP3 | ATES | NBH cooling (Qcon HP3) | Total supply | Tot demand
| kW | kW | kW | kW | kW | kW | kW | kW | [8 empty] | kW | kW | kW | kW | kW | kW | kW | kW
0:00 | 4994.7943 | 464.7293 | 0 | 1896.5987 | 3014.8455 | 548.0794 | 5459.5237 | 5459.5237 | [7 empty] | 0:00 | 558.3164 | 61.6403 | 2368.413 | 147.3809 | -2467.6997 | 571.8626 | 619.9567 | 619.9567
1:00 | 4153.1777 | 386.423 | 0 | 1577.0242 | 2414.4971 | 548.0794 | 4539.6007 | 4539.6007 | [7 empty] | 1:00 | 452.3828 | 49.9448 | 2368.413 | 119.4172 | -2557.3651 | 571.8626 | 502.3277 | 502.3277
2:00 | 4108.2412 | 382.242 | 0 | 1559.9611 | 2382.4426 | 548.0794 | 4490.4832 | 4490.4832 | [7 empty] | 2:00 | 455.0478 | 50.2391 | 2368.413 | 120.1207 | -2555.1094 | 571.8626 | 505.2869 | 505.2869
3:00 | 4420.8611 | 411.329 | 0 | 1678.6676 | 2605.443 | 548.0794 | 4832.1901 | 4832.1901 | [7 empty] | 3:00 | 463.0428 | 51.1217 | 1617.638 | 122.2312 | -1797.5672 | 571.8626 | 514.1646 | 514.1646
4:00 | 4739.2813 | 440.9557 | 0 | 1799.5766 | 2832.581 | 548.0794 | 5180.237 | 5180.237 | [7 empty] | 4:00 | 485.6953 | 53.6227 | 1617.638 | 128.2108 | -1778.3935 | 571.8626 | 539.3179 | 539.3179
5:00 | 5075.3724 | 472.2265 | 0 | 1927.1954 | 3072.3241 | 548.0794 | 5547.599 | 5547.599 | [7 empty] | 5:00 | 778.8447 | 85.9875 | 1617.638 | 205.5946 | -1530.263 | 571.8626 | 864.8322 | 864.8322
6:00 | 6971.5028 | 648.6477 | 0 | 2647.1847 | 4424.8864 | 548.0794 | 7620.1505 | 7620.1505 | [7 empty] | 6:00 | 1321.1711 | 145.8625 | 1617.638 | 348.7545 | -1115.1238 | 615.7648 | 1467.0336 | 1467.0336
7:00 | 11025.4028 | 1025.8337 | 0 | 4186.5117 | 7316.6453 | 548.0794 | 12051.2364 | 12051.2364 | [7 empty] | 7:00 | 1395.1247 | 154.0273 | 1617.638 | 368.2763 | -1127.161 | 690.3986 | 1549.152 | 1549.152
8:00 | 13640.7552 | 1269.1732 | 0 | 5179.6004 | 9182.2486 | 548.0794 | 14909.9285 | 14909.9285 | [7 empty] | 8:00 | 1495.7283 | 165.1343 | 1617.638 | 394.833 | -1112.2507 | 760.6422 | 1660.8625 | 1660.8625
9:00 | 14704.5079 | 1368.1477 | 0 | 5583.5233 | 9941.0528 | 548.0794 | 16072.6555 | 16072.6555 | [7 empty] | 9:00 | 1539.7007 | 169.989 | 1617.638 | 406.4406 | -1136.4943 | 822.1053 | 1709.6897 | 1709.6897
10:00 | 13741.7172 | 1278.567 | 0 | 5217.9372 | 9254.2676 | 548.0794 | 15020.2842 | 15020.2842 | [7 empty] | 10:00 | 1337.1611 | 147.6278 | 1617.638 | 352.9755 | -1347.4419 | 861.6173 | 1484.7889 | 1484.7889
11:00 | 12489.8067 | 1162.0858 | 0 | 4742.5679 | 8361.2451 | 548.0794 | 13651.8925 | 13651.8925 | [7 empty] | 11:00 | 1338.4936 | 147.775 | 2368.413 | 353.3272 | -2158.5521 | 923.0804 | 1486.2685 | 1486.2685
12:00 | 12200.1271 | 1135.1332 | 0 | 4632.5722 | 8154.6087 | 548.0794 | 13335.2603 | 13335.2603 | [7 empty] | 12:00 | 1374.471 | 151.747 | 2368.413 | 362.8243 | -2163.2215 | 958.2022 | 1526.218 | 1526.218
13:00 | 11852.7863 | 1102.8157 | 0 | 4500.6817 | 7906.8409 | 548.0794 | 12955.602 | 12955.602 | [7 empty] | 13:00 | 1201.2463 | 132.6223 | 2368.413 | 317.0975 | -2358.1365 | 1006.4947 | 1333.8687 | 1333.8687
14:00 | 11996.3136 | 1116.1699 | 0 | 4555.1811 | 8009.2229 | 548.0794 | 13112.4835 | 13112.4835 | [7 empty] | 14:00 | 1050.0079 | 115.925 | 2368.413 | 277.1746 | -2521.2711 | 1041.6165 | 1165.9329 | 1165.9329
15:00 | 12369.706 | 1150.9113 | 0 | 4696.9639 | 8275.574 | 548.0794 | 13520.6173 | 13520.6173 | [7 empty] | 15:00 | 1157.2739 | 127.7676 | 2368.413 | 305.49 | -2448.0388 | 1059.1774 | 1285.0415 | 1285.0415
16:00 | 12755.3361 | 1186.7914 | 0 | 4843.3934 | 8550.6546 | 548.0794 | 13942.1275 | 13942.1275 | [7 empty] | 16:00 | 1557.0231 | 171.9015 | 2368.413 | 411.0133 | -2105.2888 | 1054.7871 | 1728.9246 | 1728.9246
17:00 | 14909.4459 | 1387.2157 | 0 | 5661.3414 | 10087.2408 | 548.0794 | 16296.6616 | 16296.6616 | [7 empty] | 17:00 | 2370.5128 | 261.7139 | 2368.413 | 625.7532 | -1385.9951 | 1024.0556 | 2632.2267 | 2632.2267
18:00 | 16493.7653 | 1534.6251 | 0 | 6262.9314 | 11217.3796 | 548.0794 | 18028.3904 | 18028.3904 | [7 empty] | 18:00 | 2355.189 | 260.0221 | 2368.413 | 621.7081 | -1385.7949 | 1010.8849 | 2615.2112 | 2615.2112
19:00 | 15050.2816 | 1400.3194 | 0 | 5714.8188 | 10187.7027 | 548.0794 | 16450.601 | 16450.601 | [7 empty] | 19:00 | 1962.7686 | 216.6974 | 2368.413 | 518.1194 | -1352.7241 | 645.6576 | 2179.4659 | 2179.4659
20:00 | 14114.9657 | 1313.2951 | 0 | 5359.6653 | 9520.5161 | 548.0794 | 15428.2608 | 15428.2608 | [7 empty] | 20:00 | 1672.9504 | 184.7003 | 2368.413 | 441.615 | -1583.1101 | 630.7327 | 1857.6507 | 1857.6507
21:00 | 12716.3885 | 1183.1676 | 0 | 4828.6044 | 8522.8722 | 548.0794 | 13899.5561 | 13899.5561 | [7 empty] | 21:00 | 1399.7885 | 154.5422 | 2368.413 | 369.5074 | -1800.2269 | 616.6371 | 1554.3306 | 1554.3306
22:00 | 10231.3063 | 951.9488 | 0 | 3884.9813 | 6750.1944 | 548.0794 | 11183.2551 | 11183.2551 | [7 empty] | 22:00 | 1175.9289 | 129.8272 | 2368.413 | 310.4144 | -1987.2209 | 614.1496 | 1305.7561 | 1305.7561
23:00 | 7399.3284 | 688.4538 | 0 | 2809.6365 | 4730.0662 | 548.0794 | 8087.7822 | 8087.7822 | [7 empty] | 23:00 | 813.4896 | 89.8125 | 2368.413 | 214.7399 | -2289.8547 | 610.0038 | 903.3021 | 903.3021
Cold balance | [15 empty] | Cold balance
| VF demand (incl Win) | NBH cooling (HP3) | NBH heating (HP3) | ATES | Heat gains grid | Total supply | Total demand | [9 empty] | VF demand (incl Win) | NBH cooling (HP3) | NBH heating (HP3) | ATES | Heat gains grid | Total supply | Total demand
| kW | kW | kW | kW | kW | kW | kW | [9 empty] | kW | kW | kW | kW | kW | kW | kW
0:00 | 0 | 548.0794 | 3098.1956 | -3014.8455 | 464.7293 | 548.0794 | 548.0794 | [8 empty] | 0:00 | 2368.413 | 571.8626 | 410.9355 | 2467.6997 | 61.6403 | 2940.2756 | 2940.2756
1:00 | 0 | 548.0794 | 2576.1535 | -2414.4971 | 386.423 | 548.0794 | 548.0794 | [8 empty] | 1:00 | 2368.413 | 571.8626 | 332.9656 | 2557.3651 | 49.9448 | 2940.2756 | 2940.2756
2:00 | 0 | 548.0794 | 2548.2801 | -2382.4426 | 382.242 | 548.0794 | 548.0794 | [8 empty] | 2:00 | 2368.413 | 571.8626 | 334.9271 | 2555.1094 | 50.2391 | 2940.2756 | 2940.2756
3:00 | 0 | 548.0794 | 2742.1935 | -2605.443 | 411.329 | 548.0794 | 548.0794 | [8 empty] | 3:00 | 1617.638 | 571.8626 | 340.8117 | 1797.5672 | 51.1217 | 2189.5006 | 2189.5006
4:00 | 0 | 548.0794 | 2939.7047 | -2832.581 | 440.9557 | 548.0794 | 548.0794 | [8 empty] | 4:00 | 1617.638 | 571.8626 | 357.4845 | 1778.3935 | 53.6227 | 2189.5006 | 2189.5006
5:00 | 0 | 548.0794 | 3148.177 | -3072.3241 | 472.2265 | 548.0794 | 548.0794 | [8 empty] | 5:00 | 1617.638 | 571.8626 | 573.2501 | 1530.263 | 85.9875 | 2189.5006 | 2189.5006
6:00 | 0 | 548.0794 | 4324.3181 | -4424.8864 | 648.6477 | 548.0794 | 548.0794 | [8 empty] | 6:00 | 1617.638 | 615.7648 | 972.4166 | 1115.1238 | 145.8625 | 2233.4029 | 2233.4029
7:00 | 0 | 548.0794 | 6838.8911 | -7316.6453 | 1025.8337 | 548.0794 | 548.0794 | [8 empty] | 7:00 | 1617.638 | 690.3986 | 1026.8484 | 1127.161 | 154.0273 | 2308.0367 | 2308.0367
8:00 | 0 | 548.0794 | 8461.1548 | -9182.2486 | 1269.1732 | 548.0794 | 548.0794 | [8 empty] | 8:00 | 1617.638 | 760.6422 | 1100.8952 | 1112.2507 | 165.1343 | 2378.2802 | 2378.2802
9:00 | 0 | 548.0794 | 9120.9845 | -9941.0528 | 1368.1477 | 548.0794 | 548.0794 | [8 empty] | 9:00 | 1617.638 | 822.1053 | 1133.2601 | 1136.4943 | 169.989 | 2439.7433 | 2439.7433
10:00 | 0 | 548.0794 | 8523.78 | -9254.2676 | 1278.567 | 548.0794 | 548.0794 | [8 empty] | 10:00 | 1617.638 | 861.6173 | 984.1856 | 1347.4419 | 147.6278 | 2479.2554 | 2479.2554
11:00 | 0 | 548.0794 | 7747.2388 | -8361.2451 | 1162.0858 | 548.0794 | 548.0794 | [8 empty] | 11:00 | 2368.413 | 923.0804 | 985.1664 | 2158.5521 | 147.775 | 3291.4934 | 3291.4934
12:00 | 0 | 548.0794 | 7567.5549 | -8154.6087 | 1135.1332 | 548.0794 | 548.0794 | [8 empty] | 12:00 | 2368.413 | 958.2022 | 1011.6467 | 2163.2215 | 151.747 | 3326.6152 | 3326.6152
13:00 | 0 | 548.0794 | 7352.1047 | -7906.8409 | 1102.8157 | 548.0794 | 548.0794 | [8 empty] | 13:00 | 2368.413 | 1006.4947 | 884.1488 | 2358.1365 | 132.6223 | 3374.9077 | 3374.9077
14:00 | 0 | 548.0794 | 7441.1325 | -8009.2229 | 1116.1699 | 548.0794 | 548.0794 | [8 empty] | 14:00 | 2368.413 | 1041.6165 | 772.8333 | 2521.2711 | 115.925 | 3410.0294 | 3410.0294
15:00 | 0 | 548.0794 | 7672.7422 | -8275.574 | 1150.9113 | 548.0794 | 548.0794 | [8 empty] | 15:00 | 2368.413 | 1059.1774 | 851.784 | 2448.0388 | 127.7676 | 3427.5903 | 3427.5903
16:00 | 0 | 548.0794 | 7911.9427 | -8550.6546 | 1186.7914 | 548.0794 | 548.0794 | [8 empty] | 16:00 | 2368.413 | 1054.7871 | 1146.0099 | 2105.2888 | 171.9015 | 3423.2001 | 3423.2001
17:00 | 0 | 548.0794 | 9248.1045 | -10087.2408 | 1387.2157 | 548.0794 | 548.0794 | [8 empty] | 17:00 | 2368.413 | 1024.0556 | 1744.7596 | 1385.9951 | 261.7139 | 3392.4686 | 3392.4686
18:00 | 0 | 548.0794 | 10230.8339 | -11217.3796 | 1534.6251 | 548.0794 | 548.0794 | [8 empty] | 18:00 | 2368.413 | 1010.8849 | 1733.4809 | 1385.7949 | 260.0221 | 3379.2979 | 3379.2979
19:00 | 0 | 548.0794 | 9335.4628 | -10187.7027 | 1400.3194 | 548.0794 | 548.0794 | [8 empty] | 19:00 | 2368.413 | 645.6576 | 1444.6491 | 1352.7241 | 216.6974 | 3014.0706 | 3014.0706
20:00 | 0 | 548.0794 | 8755.3004 | -9520.5161 | 1313.2951 | 548.0794 | 548.0794 | [8 empty] | 20:00 | 2368.413 | 630.7327 | 1231.3354 | 1583.1101 | 184.7003 | 2999.1457 | 2999.1457
21:00 | 0 | 548.0794 | 7887.7841 | -8522.8722 | 1183.1676 | 548.0794 | 548.0794 | [8 empty] | 21:00 | 2368.413 | 616.6371 | 1030.281 | 1800.2269 | 154.5422 | 2985.0501 | 2985.0501
22:00 | 0 | 548.0794 | 6346.325 | -6750.1944 | 951.9488 | 548.0794 | 548.0794 | [8 empty] | 22:00 | 2368.413 | 614.1496 | 865.5145 | 1987.2209 | 129.8272 | 2982.5626 | 2982.5626
23:00 | 0 | 548.0794 | 4589.6918 | -4730.0662 | 688.4538 | 548.0794 | 548.0794 | [8 empty] | 23:00 | 2368.413 | 610.0038 | 598.7497 | 2289.8547 | 89.8125 | 2978.4168 | 2978.4168